## Manganese Assessment Tool (MAS) (hidden)
Instructions:
Manganese Assessment Tool (MAS) | 1) Click on blue cells and click on the drop down tab |  | Glossary:
| 2) Select the appropriate response for each step |  | Valid CM | Corrective Measures is valid with current source water/treatment process
3) Proceed through workbook and answer all steps
Source Water Characteristics | 4) Valid Corrective measures will appear in green |  | Valid CM with pH Adjustment | Corrective Measures is valid with the addition of a pH adjustment system
Water Source | 5) If no valid entries appear, insuffecient information provided
Number of Sources | 6) Attempt to obtain more water quality information to inform the assessment tool. If no valid entrie still appear a full assessment may be required. |  | Valid CM with Pretreatment | Corrective Measures is valid with the addition of treatment processes prior to the CM
Anoxic Hypoliminion *
Lake Turnover * |  |  | Valid CM with pH Adjust. & Pretreatment | CM is valid with the addition of a pH adjustment system and treatment processes prior to the CM
Contaminant Properties | Corrective Measures (CM) |  | Invalid CM | Corrective Measures is invalid with current source water/treatment process
Manganese Species | Selective Pumping | Invalid CM
Manganese Concentration
Frequency of Occurence | New Source Well(s) | Invalid CM
Existing Infastructure | Hypolimnetic Aeration | Invalid CM
Pre-Screening
Pre-Oxidation | Chemical Oxidation | Invalid CM
Coagualtion
Flocculation | Greensand Filter | Invalid CM
Clarification
Filtration | Multimedia + Greensand Filter | Invalid CM
Membrane
Chlorination | Ion Exchange | Invalid CM
Plant Flows | Prefiltration + Ion Exchange | Invalid CM
Flows
| PWDU/RO | Invalid CM
Water Parameters of Concern
pH | Adsorption | Invalid CM
Turbidity
Iron
DOC
* only relevant for surface water sources

## Arsenic Assessment TOOL (AAS) (hidden)
Arsenic Assessment Tool (AAS) | Instructions: |  | Glossary:
| 1) Click on blue cells and click on the drop down tab |  | Valid CM | Corrective Measures is valid with current source water/treatment process
2) Select the appropriate response for each step
Source Water Characteristics | 3) Proceed through workbook and answer all steps |  | Valid CM with pH Adjustment | Corrective Measures is valid with the addition of a pH adjustment system
Water Source | 4) Valid Corrective measures will appear in green
Number of Sources | 5) If no valid entries appear, insuffecient information |  | Valid CM with Pretreatment | Corrective Measures is valid with the addition of treatment processes prior to the CM
6) Attempt to obtain more water quality information to inform the assessment tool. If no valid entrie still appear a full assessment may be required.
Contaminant Properties |  |  | Valid CM with pH Adjust. & Pretreatment | CM is valid with the addition of a pH adjustment system and treatment processes prior to the CM
Arsenic Compound
Arsenic Species |  |  | Invalid CM | Corrective Measures is invalid with current source water/treatment process
Arsenic Concentration
Frequency of Occurence | Corrective Measures (CM)
| Selective Pumping | Invalid CM
Existing Infastructure
Pre-Screening | New Source Well(s) | Invalid CM
Pre-Oxidation
Coagualtion | Ion Exchange (IX) | Invalid CM
Flocculation
Clarification | Conventional Treatment | Invalid CM
Filtration
Membrane | Iron/Manganese Oxidation | Invalid CM
Chlorination
| Lime Softening | Invalid CM
Plant Flows
Flows | Adsoprtion Media | Invalid CM
Water Parameters of Concern | Cogulation Assissted Microfiltration | Invalid CM
pH
Turbidity | PWDU/RO | Invalid CM
Iron
Manganese
TDS
Sulfate
Calcium
Hardness
DOC

## Manganese Assessment Tool (NEW)
Manganese Assessment Tool (MAS) |  | Instructions: |  | Glossary:
|  | 1) Click on blue cells and click on the drop down tab |  | Valid CM | Corrective Measures is valid with current source water/treatment process
Town: Test |  | 2) Select the appropriate response for each step
3) Proceed through workbook and answer all steps
Source Water Characteristics |  | 4) Valid Corrective measures will appear in green |  | Valid CM with pH Adjustment | Corrective Measures is valid with the addition of a pH adjustment system
Water Source | Surface Water | 5) Inputting more information will provide a more detailed analysis and eliminate invalid CM's
Number of Sources | 1 |  |  | Valid CM with Pretreatment | Corrective Measures is valid with the addition of treatment processes prior to the CM
6) If no valid entries appear, a full assessment may be required.
Contaminant Properties |  |  |  | Valid CM with pH Adjust. & Pretreatment | CM is valid with the addition of a pH adjustment system and treatment processes prior to the CM
Manganese Species | Unknown
Manganese Concentration | All Sources, [Mn]>MAC | Corrective Measures (CM) |  | Invalid CM | Corrective Measures is invalid with current source water/treatment process
Frequency of Occurence | Continuous | Selective Pumping | Invalid CM
Existing Infastructure |  | New Source(s) | Valid CM
Pre-Oxidation | Absent
Conventional Treatment | Absent | Hypolimnetic Aeration | Valid CM
Membrane | Absent
Chlorination | Present | Chemical Oxidation | Invalid CM
Plant Flows |  | Greensand Filter | Invalid CM
Flows | > 35 L/min
|  | Multimedia + Greensand Filter | Valid CM with Pretreatment
Water Parameters of Concern
pH | 6-8 | Ion Exchange | Invalid CM
Turbidity | > 1.0 NTU
Iron | > 0.3 mg/L | Prefiltration + Ion Exchange | Invalid CM
DOC | > 3.0 mg/L
|  | PWDU/RO | Invalid CM
|  | Adsorption | Invalid CM

## Arsenic Assessment TOOL (NEW)
Arsenic Assessment Tool (AAS) |  | Instructions: |  | Glossary:
|  | 1) Click on blue cells and click on the drop down tab |  | Valid CM | Corrective Measures is valid with current source water/treatment process
2) Select the appropriate response for each step
Source Water Characteristics |  | 3) Proceed through workbook and answer all steps |  | Valid CM with pH Adjustment | Corrective Measures is valid with the addition of a pH adjustment system
Water Source | Surface Water | 4) Valid Corrective measures will appear in green
Number of Sources | 1 | 5) Inputting more information will provide a more detailed analysis and eliminate invalid CM's |  | Valid CM with Pretreatment | Corrective Measures is valid with the addition of treatment processes prior to the CM
Contaminant Properties |  | 6) If no valid entries appear, a full assessment may be required. |  | Valid CM with pH Adjust. & Pretreatment | CM is valid with the addition of a pH adjustment system and treatment processes prior to the CM
Arsenic Species | Unknown
Arsenic Concentration | All Sources [As]>MAC |  |  | Invalid CM | Corrective Measures is invalid with current source water/treatment process
Frequency of Occurence | Continuous
Corrective Measures (CM)
Existing Infastructure |  | Selective Pumping | Invalid CM
Pre-Screening | Absent
Pre-Oxidation | Absent | New Source(s) | Valid CM
Conventional Treatment | Absent
Membrane | Absent | Ion Exchange (IX) | Invalid CM
Chlorination | Present
|  | Conventional Treatment | Valid CM with Pretreatment
Plant Flows
Flows | > 35 L/min | Iron/Manganese Oxidation | Invalid CM
Water Parameters of Concern |  | Lime Softening | Valid CM with pH Adjust. & Pretreatment
pH | 6-8
Turbidity | > 1.0 NTU | Adsoprtion Media | Invalid CM
Iron | > 0.3 mg/L
Manganese | > 0.02 mg/L | Cogulation Assissted Microfiltration | Invalid CM
TDS | > 250 mg/L
Sulfate | < 40 mg/L | PWDU/RO | Invalid CM
Calcium | Absent
Hardness | > 60 mg-CaCO3/L
DOC | > 3.0 mg/L

## WQ Data
Community:
Source:
Date:
Parameter | Units
Alkalinity | mg/L
Colour | TCU
Conductivity | uS/cm
Hardness | mg/L
pH
TDS | mg/L
Turbidity | NTU
DOC | mg/L
Iron | mg/L
Manganese | mg/L
Arsenic | mg/L
Calcium | mg/L
Sulphate | mg/L

## Technology Description
Technology Descriptions (Manganese)
Selective Pumping | Chemical Oxidation | Ion Exchange | Manganese Adsorption
Selective pumping is a simple corrective measure that consists of increased pumping from wells that meet manganese drinking water standards. This is only possible for communities containing multiple wells, in which not all source wells exceed manganese guidelines. The best course of action is to decrease pumping on wells with high manganese concentrations, and simultaneously, increase pumping on wells with low manganese concentrations. | Dissolved manganese (Mn(II)) is the most common form entering a treatment plant and is very stable under various temperatures, pH and dissolved oxygen ranges. Dissolved manganese can be oxidized by one or more chemical oxidants into insoluble forms of manganese (Mn(III) & Mn(IV)). Insoluble forms are subsequently removed using solid-liquid separation techniques such as multimedia filtration or membranes. Various chemicals can oxidize dissolved manganese, including permanganate, chlorine dioxide, ozone and free chlorine. | Ion exchange is a treatment process in which undesirable ions, including manganese, exchange places with a harmless ion on a solid exchange resin. The cationic exchange occurs on a continuous basis until the media is exhausted. Once exhaustion is reached, the resin undergoes a recharge phase to remove the target ion from the media and replace it with more harmless ions. Various natural ions will compete with manganese for adsorption on the resin, and as such, low turbidity and low DOC waters are desirable. | Manganese adsorption acts on a similar principle to greensand filters and utilizes a media with a manganese oxide coating to absorb dissolved manganese. The use of absorptive media in post filter contactors has been proven to efficiently remove dissolved manganese. Manganese absorptions works best when Mn(II) is the primary constituent and there is low turbidity and low DOC condtions.
.
New Source(s)
This corrective measure involves drilling new source wells that produce drinking water that meets manganese drinking water standards. A hydrogeological assessment in tandem with test well sampling could identify possible locations for new wells for a community. This method has the possibility to resolve manganese issues in drinking water, but may result in new drinking water issues, such as arsenic from groundwater or lead descaling from lead pipes. |  | Ion Exchange + Prefiltration
| Greensand Filter | Ion exchange (IX) is a treatment process in which undesirable ions, including manganese, exchange places with a harmless ion on a solid exchange resin. The cationic exchange occurs on a continuous basis until the media is exhausted. Once exhaustion is reached, the resin undergoes a recharge phase to remove the target ion from the media and replace it with harmless ion. Various natural ions will compete with manganese for adsorption on the resin, in source waters with high turbidities, prefiltration can significantly improve IX performance.
Greensand filters are a traditional method used to remove dissolved manganese (Mn(II)). Greensand filters function on the principle of adsorption and absorb dissolved Mn particles onto a manganese oxide (MnOx) coating on the sand. As the media absorbs manganese over time, it eventually requires to be regenerated, which commonly achieved using chlorine. Direct greensand filtration is commonly used on groundwater sources with low turbidity.
Hypolimnetic Aeration
Manganese in surface waters is often released from chemical reactions in the sediment of deep anoxic zones (no oxygen). During the spring and fall, lake turnover mixes the entire depth of the lake, releasing manganese into the shallower depths of the lake, which can enter drinking water supplies. Hypolimnetic aeration is a corrective measure that prevents manganese release in the deep zones through aeration. Hypolimnetic aeration requires the installation of a permanent aeration device in the source water to stop the chemical reactions that release manganese from sediments.
Greensand Filter + Multimedia Filter
Greensand filters are a traditional method used to remove dissolved manganese (Mn(II)). Greensand filters function on the principle of adsorption and absorb dissolved Mn particles onto a manganese oxide(MnOx) coating on the sand. As the media absorbs manganese over time, it eventually requires to be regenerated, which commonly achieved using chlorine. Surface water with high turbidity, will often require multimedia filtration alongside greensand filtration to remove solid particulate and manganese simultaneously.
PWDU/RO
Portable water dispensing units (PWDU) are small scale water treatment systems that treat a fraction of the demand for a community. PWDUs are not connected to a communities supply system and require residents to collect the high quality drinking water from the PWDU. PWDU typically include a filtration system, reverse osmosis and a disinfectant. PWDU are capable of removing manganese from source water and function best with a low DOC water supply.
Technology Descriptions (Arsenic)
Selective Pumping | Conventional Treatment | Adsorptive Media
Selective pumping is a simple corrective measure that consists of increased pumping from wells that meet arsenic drinking water standards. This is only possible in communities containing multiple wells, in which not all source wells exceed arsenic guidelines. In this scenario, it is recommended that pumping be decreased on wells with high manganese concentrations, and simultaneously, pumping be increased on wells with low manganese concentrations. | Conventional Treatment utilizing coagulation and filtration can be optimized to remove dissolved inorganic arsenic (As(V)) from drinking water. Arsenic can be precipitated using various coagulants into larger flocs which are subsequently removed by liquid-solid separation techniques (ie. filtration or membranes). Removal of arsenic using this method requires pre-existing treatment infrastructure or significant capital investment to construct a new water treatment plant, which is often not viable. | Adsorptive media, commonly using activated alumina (AA), is an arsenic removal method that uses a porous media to remove arsenic ions from water. AA is produced from aluminum hydroxide and has large surface area that traps arsenic within the pore structure. Overtime, AA media will begin to exhaust and become less efficient, requiring regeneration or replacement. To increase the lifespan, AA functions best in a low turbidity and low DOC environment with dissolved inorganic arsenic.
New Source(s) | Iron/Manganese Oxidation | Cogulation Assissted Microfiltration
This corrective measure involves drilling new source wells that produce drinking water that meets arsenic drinking water standards. A hydrogeological assessment in tandem with test well sampling could identify possible locations for new wells for a community. This method has the possibility to resolve manganese issues in drinking water, but may result in new drinking water issues, such as arsenic from groundwater or lead descaling from lead pipes. | The oxidation of iron and manganese into insoluble forms within drinking water, has the side effect of removing arsenic at the same time. The addition of an oxidant will first oxidize As(III) into soluble As(V). Following this, soluble As(V) is absorbed onto the precipitated iron/manganese and removed using solid-liquid separation. Iron is more efficient than manganese at removing arsenic and the oxidation process is sensitive to pH, the presence of sulfate and the concentration of iron and/or manganese. | Coagulation assisted microfiltration utilizes oxidation and solid-liquid separation to remove arsenic. Oxidation can be used to oxidize As(III) to As(V) is necessary. The addition of coagulant precipitates arsenic, which is subsequently retained on the microfiltration unit. Backwashing must be performed periodically to remove the precipitated arsenic from the filters. Coagulation assisted microfiltration works best in low turbidity waters and can help in the removal of other organic and inorganic compounds in the water.
Ion Exchange (IX)
Ion exchange is a treatment process in which undesirable ions, including arsenic, exchange places with a harmless ion on a solid exchange resin. The cationic exchange occurs on a continuous basis until the media is exhausted. Once exhaustion is reached, the resin undergoes a recharge phase to remove the target ion from the media and replace it with harmless ion. Various natural ions will compete with manganese for adsorption on the resin, and as such, low turbidity and low DOC waters are desirable.
| Lime Softening | PWDU/RO
| Lime Softening is another precipitative method to remove arsenic from drinking water. The addition of lime to water is traditionally used to remove the various ions that cause hardness, including calcium and magnesium. The high pH conditions caused by lime addition promote the coprecipitation of arsenic alongside the target hardness compounds. Lime softening is not recommended unless a water utility is already dealing with hard water due to financial costs of lime softening. | Portable water dispensing units (PWDU) are small scale water treatment systems that treat a fraction of the demand for a community. PWDUs are not connected to a communities supply system and require residents to collect the high quality drinking water from the PWDU. PWDU typically include a filtration system, reverse osmosis and a disinfectant. PWDU are capable of removing Arsenic from source water and function best with a low turbidity and low DOC water supply.

## Manganese Data
source water characteristics | Plant Flows
Surface Water | < 35 L/min
Ground Water | > 35 L/min
Mixed
Unsure | Turbidity
> 1.0 NTU
Number of Sources | < 1.0 NTU
1 | Unknown
>1
Unsure | Iron
> 0.3 mg/L
Anoxic Hypolimnion | < 0.3 mg/L
Yes | Unknown
No
Unknown | DOC
> 3.0 mg/L
Lake Turnover | < 3.0 mg/L
Yes | Unknown
No
Unknown | pH
> 10
manganese species | 8-10
Dissolved (Mn(II)) | 6-8
Particulate (MnOx) | 4-6
Unknown
Manganese Concentration
All Sources, [Mn]>MAC
Not All Sources, [Mn]>MAC
Frequency of Occurence
Seasonal
Continuous
Pre-Screening
Present
Absent
Unknown
Pre-Oxidation
Present
Absent
Unknown
Coagualtion
Present
Absent
Unknown
Flocculation
Present
Absent
Unknown
Clarification
Present
Absent
Unknown
Filtration
Present
Absent
Unknown
Membrane
Present
Absent
Unknown
Chlorination
Present
Absent
Unknown

## Arsenic data
source water characteristics | Plant Flows
Surface Water | < 35 L/min
Ground Water | > 35 L/min
Mixed
Unsure | pH
> 10
Number of Sources | 8-10
1 | 6-8
>1 | 4-6
Unsure
Turbidity
Arsenic Compound | > 1.0 NTU
Organic Arsenic | < 1.0 NTU
Inorganic Arsenic | Unknown
Combined
Unknown | Iron
> 0.3 mg/L
Arsenic Species | < 0.3 mg/L
As(III) | Unknown
As(V)
Unknown | Manganese
> 0.02 mg/L
Arsenic Concentration | < 0.02 mg/L
All Sources [As]>MAC | Unknown
Not All Sources [As]>MAC
TDS
Frequency of Occurrence | > 250 mg/L
Seasonal | < 250 mg/L
Continuous | Unknown
Pre-Screening | Sulfate
Present | > 40 mg/L
Absent | < 40 mg/L
Unknown | Unknown
Pre-Oxidation | Calcium
Present | Present
Absent | Absent
Unknown | Unknown
Coagualtion | Hardness
Present | > 60 mg-CaCO3/L
Absent | < 60 mg-CaCO3/L
Unknown | Unknown
Flocculation | DOC
Present | > 3.0 mg/L
Absent | < 3.0 mg/L
Unknown | Unknown
Clarification
Present
Absent
Unknown
Filtration
Present
Absent
Unknown
Membrane
Present
Absent
Unknown
Chlorination
Present
Absent
Unknown