## CT Calculator
Disinfection Compliance Calculator |  |  | Calculation Method
Defaults |  |  | Title | PRP - Gumbel
|  |  | Source | Zhang (2005)
CT Required | 6 |  | Year | 2005
Default per capita water use | 340 | Lpcd | Population Range | 1,000 <= P <= 25,000
Variables
ENVC Inputs |  |  | P | Population
Equation
Contact volume | 1488.8118 | L
Population | 300
Per capita water use |  | Lpcd
Peak recorded water use |  | L/min
User Inputs
Chlorine residual | 1.2 | mg/L
pH | 7
Temperature | 18.2 | oC
Outputs
Average day flow | 102000 | L/day
Peaking factor | 6.4801
Peak flow | 459.0083 | L/min
Effective contact time | 3.2435 | min
CT achieved | 3.8922
Inactivation ratio | 0.64871
Log Inactivation
Giardia | 0.17828 | log
Viruses | 4.8005 | log
Compliance
CT = 6 | No
CT = 12 | No

## Log Reduction-Based
Disinfection Compliance Calculator
Defaults
Default per capita water use | 340 | Lpcd
LR required (Giardia) | 3
LR required (viruses) | 4
ENVC Inputs
Log reduction achieved by treatment
Giardia | 0
Viruses | 0
Effective contact volume | 1488.8118 | L
Population | 227
Per capita water use |  | Lpcd
Peak recorded flow |  | L/min
User Inputs
Chlorine residual | 0.02 | mg/L
pH | 8
Temperature | 0.5 | oC
Outputs
Log inactivation required
Giardia | 3
Viruses | 4
Average day flow | 77180 | L/day
Peaking factor | 7.0756
Peak flow | 379.23 | L/min
Effective contact time | 3.9259 | min
CT required
Giardia | 173.2207
Viruses | 12.9472
Compliance
CT achieved | 0.078518
Inactivation ratio
Giardia | 0.00045328
Viruses | 0.0060644

## Contact Volume Calculator
Total |  |  |  | Unit Conversions
System Components |  |  |  | Inputs |  | Outputs
Transmission Main | 1.4888 | m3 |  |  | ft | 0 | m
Reaction Tank | 0 | m3 |  |  | in | 0 | mm
Clearwell | 0 | m3 |  |  | USGal | 0 | m3
Storage | 0 | m3 |  |  | ft3 | 0 | m3
Other |  | m3 |  |  | IGal | 0 | m3
Total Effective Volume | 1.4888 | m3 |  |  | L | 0 | m3
[5 empty] | m3 | 0 | L
Transmission Main
Dimensions
Pipe Diameter | 203 | mm
Pipe Length | 46 | m
Volume
Total Volume | 1.4888 | m3
Reaction Tank |  |  | Clearwell |  |  |  | Storage*
Volume (known) |  |  | Volume (known) |  |  |  | Volume (known)
| 28.3 | m3 |  |  | m3 |  |  |  | m3
Shape ('x') |  |  | Shape ('x') |  |  |  | Shape ('x')
Cylindrical |  |  | Cylindrical |  |  |  | Cylindrical
Rectangular |  |  | Rectangular |  |  |  | Rectangular
Dimensions |  |  | Dimensions |  |  |  | Dimensions
Height |  | m | Height |  | m |  | Height |  | m
Length |  | m | Length |  | m |  | Length |  | m
Width |  | m | Width |  | m |  | Width |  | m
Diameter |  | m | Diameter |  | m |  | Diameter |  | m
Baffling Factor |  |  | Baffling Factor |  |  |  | Baffling Factor
Volume |  |  | Volume |  |  |  | Volume
Total Volume | 28.3 | m3 | Total Volume | 0 | m3 |  | Total Volume | 0 | m3
Effective Volume | 0 | m3 | Effective Volume | 0 | m3 |  | Effective Volume | 0 | m3
*after chlorination, before first user

## Baffling Factor
Baffling Factor | Inlet/Outlet | Intra-basin Baffles | Mixing | Notes | Schematic
0.3 | Single or multiple unbaffled inlets and outlets | None | Minimal | Short circuiting and stagnation are likely to occur
0.5 | Single or multiple baffled inlets and/or outlets | Some | Moderate
0.7 | Perforated inlet baffle, outlet weir, perforated launders | Serpentine, perforated | Superior
1 | n/a | n/a | Total | Plug-flow