# GENERAL

## SUMMARY

### Section Includes

#### General requirements relating to commissioning of project's components and systems, specifying general requirements for Installation Verification and Performance Verification of components, equipment, sub-systems, systems, and integrated systems.

### Acronyms

#### CxA – Commissioning Authority.

#### Cx – Commissioning.

#### EMCS – Energy Monitoring and Control Systems.

#### O&M – Operation and Maintenance.

#### PV – Performance Verification.

#### TAB – Testing, Adjusting and Balancing.

#### GC – General Contractor

#### TSI – Technical Services Inspector

#### LEED - Leadership in Energy and Environmental Design

## COMMISSIONING INTENT

### Undertake Cx to bring the facility to a fully operational state and free of deficiencies in the most effective and timely manner available, ensuring the design intent is met by all systems.

### Cx incorporates inspection and quality assurance activities as construction progresses, including start up, installation verification, performance verification, fine tuning, and operator training.

### Bear all costs associated with the required personnel and test equipment as outlined in specification sections and Cx Manual and all costs with organizing and managing the activities of the applicable subtrades as identified in this section.

### Fully document all tests and inspections performed during the construction, at start up, installation verification and performance verification and fine tuning. Incorporate into final commissioning documentation.

### Provide direct training to designated staff responsible for the operation and maintenance of the building equipment and systems.

## RELATED SECTIONS

### Section 01 45 00 - Quality Control.

### Section 01 77 00 - Closeout Procedures.

### Section 01 78 00 - Closeout Submittals.

### Section 01 79 00.13 – Demonstration and Training for Building Commissioning.

### Section 01 91 13.16 - Commissioning (Cx) Forms.

## COMMISSIONING OVERVIEW

### Cx is a planned program of tests, procedures and checks carried out systematically on systems and integrated systems of the finished project.

### Cx is an intensive quality assurance process that begins at the beginning of the project and continues through to the first year of occupancy. The process focuses upon verifying and documenting that the facility and all of its systems and assemblies are planned, designed, installed, tested, operated, and maintained to meet the Owners Project Requirements.

### Cx activities supplement field quality and testing procedures described in relevant technical sections.

### Cx identifies issues in Planning and Design stages which are addressed during Construction and Cx stages to ensure the built facility is constructed and proven to operate satisfactorily under weather, environmental and occupancy conditions to meet functional and operational requirements. Cx activities include transfer of critical knowledge to facility operational personnel.

### Complete inspection and verification activities as required by the specifications and Cx Manual as construction progresses.

### Take responsibility to:

#### Review the Cx manual with the commissioning team.

#### Complete all items as identified in the Cx manual.  This includes work by subcontractors, test agencies, equipment representatives and manufacturer agents.

#### Review Contract Documents and inspect the Work to ensure completeness of the Work and compliance with the Contract Documents.

#### Correct deficiencies resulting from installation and performance verifications.

#### Test, adjust and balance equipment and systems identified in Divisions 2-44.

#### Submit the completed manual and project record documents as specified.

#### Update the documentation manuals prior to each project meeting.

### The Substantial Completion Certificate will not be issued until the commissioning process is completed and the final reports and commissioning documentation are received.

### The Cx Manual provides direction for the Cx process during design and construction, provides resolution for issues such as scheduling, roles and responsibilities, lines of communication and reporting, approvals and coordination.

## COMMISSIONING TEAM

### The commissioning team shall consist of: (as applicable to project)

#### Department Representative(s):

##### Design Manager (DM).

##### Construction Manager (CM).

##### Project Coordinator (PC).

##### Engineer/Architect/Consultant (AE).

##### Technical Services Inspectors (TSI).

#### User Representatives/Owner.

#### General Contractor (GC):

##### Mechanical Contractor.

##### Fire Protection Contractor.

##### Controls Contractor (CC).

##### Electrical Contractor.

##### Fire Alarm Contractor.

##### Security Systems Contractor.

##### Communications Systems Contractor.

#### Commissioning Authority (CxA).

#### Manufacturer’s Technicians.

#### Testing Agencies.

#### Building Manager (BM).

#### Design Consultant (DC).

### Roles of the commissioning team shall be as follows:

#### CxA (Commissioning Authority):

##### Reviews Owner’s Project Requirements, Basis of Design and design documents at all stages of submittal and provides comments to the DM.

##### Records all comments as history for the project commissioning.

##### Produces the Commissioning Manual for review by the DM and DC, and modifies based on their comments as necessary.

##### Provides “Issued for Construction” Commissioning Manual to the DM.

##### Provides guidance on the Commissioning Process, and responsibilities of Commissioning Team members.

##### Reviews contractor shop drawings for related commissioning information.

##### Coordinates and chairs (in person or via teleconference) the commissioning kick-off meeting and progress meetings.

##### Prepares and distributes the meeting agenda and minutes.

##### Attends when necessary Installation Verification.

##### Reviews completed Installation Verification checklists and signs off.

##### Attends Performance Verification and signs off on check lists.

##### Attends owner training sessions.

##### Verifies that training is complete.

##### Reviews completed Cx manual as submitted by the contractor.

##### Prepares Summary Commissioning Report and submits to the CM.

##### Prepares letter for CM indicating acceptance of the completed commissioning activities.

##### Verifies that seasonal or deferred Commissioning is completed.

##### Coordinates ten (10) month building review and issues occupant survey.

#### DM (Design Manager):

##### Reviews Owner’s Project Requirements, Basis of Design and design documents at all stages of submittal. Compiles all comments from all reviewers and submits to document originator.

##### Submits all documentation required by the CxA in a timely manner.

##### Identifies Cx team members.

##### Provides a list of equipment and systems included in the design to the CxA for inclusion in preliminary manual.

##### Reviews Cx manual in draft and final revisions. Provides comments to the CxA as necessary on the Commissioning Manual.

##### Forwards the Cx Manual for review by the DC, receives comments and issues them to the CxA.

##### Ensures that the Cx Manual is issued with the tender documents.

##### Issues IFC Cx Manual to the CM.

##### Reviews contractor shop drawings and provide comments to the CM.

##### Attends Cx kick-off meeting during the design phase.

##### Attends commissioning progress meetings as required.

##### Attends Installation Verification as required.

##### Attends Cx Performance Verification or provides representative.

##### Attends training sessions or sends representative knowledgeable in the design.

##### Assists with ten (10) month building review.

#### CM (Construction Manager):

##### Main contact for CxA during construction phase.

##### Distributes “Issued for Construction” Cx Manual to GC.

##### Notifies CxA of any Cx related issues raised during construction (i.e. change orders).

##### Provides times during any project meetings to discuss Cx with the entire team.

##### Attends Cx meetings (construction phase).

##### Coordinates Cx schedule for Installation Verification and Performance Verification with GC and ensures all TI representatives are available to witness testing as required for Installation Verification and Performance Verification.

##### Attend Performance Verification.

##### Ensures Cx Team is following/completing Cx Manual.

##### Coordinates training schedules, and arranges for video recording of sessions if required.

##### Reviews project record documents.

##### Ensures that O&M manuals, maintenance materials, as-built drawings and warranties have been submitted and reviewed.

##### Provides CxA with reviewed As Built documents, O&M Manuals, and Warranties for inclusion in the Summary Commissioning Report.

##### Receives the completed Cx Manual from the GC and submits to the CxA for review.

##### Receives the Summary Commissioning Report from the CxA and submits to the Owner.

##### Coordinates ten (10) month building review and issues occupant survey.

##### Verifies that all maintenance materials, spare parts and tools are received from the GC as per specifications.

#### BM (Building Manager):

##### Reviews the Basis of Design developed by the DC and provides comments to the DM.

##### Reviews all design documents and provides comments to the DM.

##### Coordinates maintenance staff participation in Cx activities.

##### Reviews O&M documentation and attends training.

##### Attends all training sessions.

##### Receives and retains a copy of the Commissioning Summary Report.

##### Provides maintenance representatives to facilitate the 10 month building review as necessary.

##### Attends commissioning meetings as necessary.

#### GC (General Contractor):

##### Maintains as-built drawings on site during construction.

##### Submits shop drawing in accordance with the specifications.

##### Ensures the Cx Manual is on site and being completed and kept up to date by all sub-trades.

##### Executes the Cx process ensuring that sub-trades perform their responsibilities and integrate Cx into the construction process.

##### Ensures equipment manufacturers and vendors provide documentation to facilitate the Commissioning work and perform startups.

##### Coordinates and schedules Cx activities, submits schedule for review and comment by TI staff.

##### Conducts Installation Verification and signs off checklists.

##### Provides written confirmation all systems are operational prior to start of Performance Verification.

##### Conducts Performance Verification with all required Commissioning Team members present.

##### Ensures that all required personal are available for the verification.

##### Maintains an up to date version of the Cx manual on site with checklists completed on installed/operational systems.

##### Provides all required training.

##### Coordinates location, schedule.

##### Provides facilities (location, materials).

##### Ensures qualified factory trained technicians are available to facilitate training.

##### Provides copies of all training material.

##### Obtains occupancy approvals/permits.

##### Submits completed manual to CM.

##### Provides the following information for inclusion in the Commissioning Summary Report.

##### Training Records.

##### Operation and Maintenance Manuals.

##### Warranties.

##### Completed commissioning Checklists.

##### List of spare parts turned over.

##### Supplies maintenance materials and tools as per specification.

##### Attends all commissioning meetings.

#### PC (Project Coordinator):

##### If there is no PC assigned to the project, then these duties are completed by the CM.

##### Attends Installation Verification and Performance Verification demonstrations.

##### Ensures Cx manual is on site and kept up to date by the GC.

##### Verifies maintenance materials are provided by the GC as per the contract documents.

##### Ensures GC is maintaining as-built drawings on site during construction.

##### Attends training sessions as necessary and directed by the CM.

##### Attends all commissioning meetings.

#### TSI (Technical Services Inspector):

##### Attends Installation Verification and Performance Verification for equipment within their discipline.

##### Signs off on commissioning checklists within their discipline.

##### Attends training sessions as necessary and directed by the CM.

##### Attends all commissioning meetings.

#### Sub Trades:

##### Demonstrates correct system performance.

##### Perform commissioning duties as directed by the GC.

#### DC (Design Consultant):

##### Reviews the Owner Project Requirements and provides comment to the DM.

##### Produces the Basis of Design and submits to the DM for review and comment. Revise as necessary based on comments and changes in Owner Project Requirements.

##### Develops system descriptions and forwards to the CxA, for inclusion in the Cx Manual.

##### Reviews drafts of the Cx Manual, including the installation and Performance Verification checklists, and provides comments to the DM.

##### Provides project narrative for inclusion in the Cx Manual.

##### The DC shall provide to the CxA a complete list of all equipment and information required to populate the commissioning checklists with the following information:

###### identification number.

###### location.

###### type, proposed manufacture, make, model.

###### operating parameter (max, normal, min).

###### electrical requirements.

###### control comments.

###### other pertinent information.

##### Incorporates commissioning specification into the project documents.

##### Reviews contractor shop drawing submittals.

##### Attends periodic site visits to ensure systems meet the design intent and operate as outline in the specifications.

##### Attends and signs off checklist for Installation Verification.

##### Attends Performance Verification and signs off on checklists for the appropriate discipline.

##### Develops and submits Systems Manuals to the CM (these will be included in the Commissioning Summary Report).

##### Provides system overview during training.

##### Attends training as required.

##### Attends commissioning meetings.

##### Attends ten (10) month building review activities.

#### Owner:

##### Produces the Owner Project Requirements and submits to the DM.

##### Reviews the Basis of Design developed by the DC and provides comments to the DM.

##### Reviews all design documents and provides comments to the DM.

##### Coordinates maintenance staff participation in Cx activities.

##### Reviews O&M documentation and attends training.

##### Attends all training sessions.

##### Receives and retains a copy of the Commissioning Summary Report.

##### Provides maintenance representatives to facilitate the ten (10) month building review as necessary.

##### Attends commissioning meetings as necessary.

## NON-CONFORMANCE TO PERFORMANCE VERIFICATION REQUIREMENTS

### During Cx, should equipment, system components, and  associated controls be identified as incorrectly installed, malfunctioning or not performing as per specifications, the contractor shall correct deficiencies, re-verify equipment and components within the system, including related systems as deemed necessary by the Owner, to ensure effective and accurate operation.

### Minor deficiencies may be corrected at the time of identification.  For systems requiring major repairs, the Commissioning Team shall move on to the next system to be commissioning.  The Contractor shall notify the CM when the work is complete.

### Costs for corrective work, additional tests, inspections, to determine acceptability and proper performance of such items to be borne by Contractor.

## CONFLICTS

### Report conflicts between requirements of this section, other sections, and the Cx Manual to the CM to obtain clarification prior to the start of work.

### Failure to report conflict and obtain clarification will result in application of most stringent requirement.

## SUBMITTALS

### Prior to starting Cx the Contractor shall provide a set of equipment and system submittals. These submittals are supplemented by the installation and start-up procedures, O&M data, performance data, control drawings and any changes that may affect commissioned systems.

### Submit no later than four (4) weeks after award of Contract:

#### Name of Contractor's Cx coordinator.

#### Preliminary Cx schedule. Submit final Cx schedule to CxA for review prior to performance verification.

#### Submit the names of all personnel for approval by the CxA. Designate who has managerial responsibilities for coordination of installation verification and performance verification.

#### Submit documentation to confirm personnel compliance with quality assurance provisions.

### Any changes to the information submitted must be re-submitted Ensure certified trades persons, certified testing agencies and/or factory authorized personnel participate in commissioning tasks.

### Prior to start of Performance Verification:

#### Submit TAB report to CxA for review.

#### Submit start-up documentation to CxA for review.

#### Submit completed Installation Verification checklists.

### Fifteen (15) days prior to application for Substantial Completion:

#### Submit three (3) copies of final commissioning manual and applicable forms to the CM for review.

#### Submit reports of performance verifications postponed due to seasonal, climatic, occupancy, or other reasons beyond the Contractor’s control, promptly after execution of those services.

### Ensure each form bears the required signatures as indicated on the form.

### Submit as-built drawings, schematics, O&M manuals, maintenance materials and warranties to CM for review.

### Where structurally attached equipment is included in the scope of work, engage a third party Professional Structural Engineer, licensed to practice in the Province of Newfoundland and Labrador, for submission of stamped and signed shop drawings indicating acceptable mounting procedures for all equipment which is suspended, mounted or otherwise attached, as per Section 01 33 00 – Submittal Procedures. The Structural Engineer to also verify correct installation of the equipment.

## COMMISSIONING DOCUMENTATION

### Refer to Section 01 91 13.16 - Commissioning (Cx) Forms for requirements and instructions for use as well as the Cx Manual

### Checklists will be provided to the Contractor by the CM during the construction stage.

### Installing subcontractors are to date and initial the checklists as construction and verifications are completed.

### The general contractor is to submit completed checklists to the CxA for review and acceptance.

### Once all documents have been reviewed and accepted the general contractor shall submit final commissioning documents in electronic form (PDF) and original signed copies.

## COMMISSIONING SCHEDULE

### Submit preliminary Cx schedule in Gantt Chart format to CxA no later than four (4) weeks after award of contract. A sample Cx Schedule is provided in the Cx Manual.

### Submit final Cx schedule in Gantt Chart format to CxA for review four (4) weeks prior to performance verification. A sample Cx Schedule is provided in the Cx Manual.

### Provide adequate time for Cx activities prescribed in technical sections, commissioning sections and the Cx manual including all on site activities as well as documentation procedures. Time should be allowed for re-verification should any system be rejected upon completion of initial verification.

### Provide adequate time for training.

## COMMISSIONING MEETINGS

### The CM will convene Cx meeting consisting of all members of the design and construction teams to address building systems to be commissioned. Items to be discussed will include commissioning requirements, completion and start-up schedules, and roles and responsibilities.

### CxA to make necessary updates and changes to the CxManual and deliver to the CM who will distribute to all other parties as necessary.

### Convene Cx meetings following project meetings and as specified herein to resolve issues, monitor progress and identify deficiencies relating to Cx.

### Continue Cx meetings on regular basis until commissioning deliverables have been addressed.

### At 60% construction completion stage CxA to call a separate Cx meeting to review progress, discuss schedule of equipment start-up activities and prepare for Cx.  Issues at meeting to include:

#### Review duties and responsibilities of Contractor and subcontractors, addressing delays and potential problems.

#### Determine the degree of involvement of trades and manufacturer's representatives in the commissioning process.

### Thereafter Cx meetings to be held until project completion and as required during equipment start-up and functional testing period.

### Meetings will be chaired by the CxA or CM, meeting minutes will be prepared and issued by the CxA or CM.  Clarifications to the minutes must be submitted within 5 days of issue, after which, the issued set becomes the official project record.

### Ensure subcontractors and relevant manufacturer representatives are present at 60% and subsequent Cx meetings and as required.

## STARTING AND TESTING

### Contractor assumes liabilities and costs for inspections, including disassembly and re-assembly after approval, starting, testing and adjusting, and supply of testing equipment, and all associated costs of installation and performance verification.

## WITNESSING OF STARTING AND TESTING

### Provide twenty eight (28) days’ notice prior to commencement.

### Owner to witness start-up and testing.

### Contractor's Cx Coordinator to be present at tests performed and documented by sub-trades, suppliers and equipment manufacturers.

## MANUFACTURER'S INVOLVEMENT

### The Contractor shall obtain manufacturers installation, start-up and operations instructions prior to start-up of components, equipment and systems.

#### Compare completed installation with manufacturer's published data, record discrepancies, and review with manufacturer.

#### Modify procedures detrimental to equipment performance and review same with manufacturer before start-up.

### Integrity of warranties:

#### Use manufacturer's trained start-up personnel where specified elsewhere in other divisions or required to maintain integrity of warranty.

#### Verify with manufacturer that testing as specified will not void warranties.

### Qualifications of manufacturer's personnel:

#### Experienced in design, installation and operation of equipment and systems.

#### Ability to interpret test results accurately.

#### Ability to report results in clear, concise, logical manner.

## PROCEDURES

### Verify that equipment and systems are complete, clean, and operating in normal and safe manner prior to conducting Performance Verification.

### Conduct Commissioning in following distinct phases:

#### Included in delivery and installation:

##### Verification of conformity to specification, approved shop drawings and completion of product information report forms.

##### Visual inspection of quality of installation.

#### Installation Verification: follow accepted start-up procedures.

#### Performance Verification: document equipment performance.  Include repetition of tests after correcting deficiencies.

#### Post-substantial performance verification: to include fine-tuning.

### Correct deficiencies and obtain approval from CxA after distinct phases have been completed and before commencing next phase.

### Document required tests on checklists provided in the Cx Manual as well on any supplied Manufacturer forms.

### Failure to follow accepted Commissioning Processes will result in re-evaluation of equipment by an independent testing agency selected by CxA. If results reveal that equipment Commissioning Process was not in accordance with requirements, and resulted in damage to equipment, implement following:

#### Minor equipment/systems: if evaluation report concludes that damage is minor, implement corrective measures approved by CxA.

#### Major equipment/systems:  If evaluation report concludes that major damage has occurred, CxA shall reject equipment to be removed from site and replaced with new.

#### Subject new equipment/systems to specified Commissioning Process

## Commissioning DOCUMENTATION

### Assemble Installation Verification documentation and submit to CxA for approval before commencement of Performance Verification.

### Installation Verification documentation to include:

#### Factory and on-site test certificates for specified equipment.

#### Inspection reports.

#### Signed Installation Verification check lists.

#### Start-up reports.

#### Step-by-step description of complete start-up procedures, to permit the contractor or CxA to repeat start-up at any time.

## OPERATION AND MAINTENANCE OF EQUIPMENT AND SYSTEMS

### After Performance Verification, operate and maintain equipment and systems as directed by equipment/system manufacturer.

### With assistance of manufacturer develop written maintenance program and submit to CxA for approval before implementation.

### Operate and maintain systems for minimum twenty one (21) days for commissioning to be completed.

### After completion of commissioning, operate and maintain systems until issuance of Substantial Completion

## TEST RESULTS

### If start-up, testing and/or performance verification produce unacceptable results, repair, replace or repeat specified starting and/or performance verification procedures until acceptable results are achieved.

### Provide personnel, resources and materials, assume all costs for re-verification.

## INSTRUMENTS / EQUIPMENT

### Submit to CxA for review and approval:

#### Complete list of instruments proposed to be used.

#### Listed data including, serial number, current calibration certificate, calibration date, calibration expiry date and calibration accuracy.

### Provide all required equipment to complete commissioning.

### Provide all Arc Flash Personal Protective Equipment as required. Provide commissioning personnel with the appropriate Arc Flash Protection training.

## PERFORMANCE VERIFICATION

### Notify CxA at least twenty eight (28) days prior to start of Performance Verifications.

### Start Performance Verification after elements of building affecting start-up and performance verification of systems have been completed.

### Ensure all HVAC systems have been thoroughly cleaned.

### Conduct performance verification once identified pre-requisite activities are completed for a system and approved by the CxA.

### Test all building systems including architectural, structural, civil, mechanical and electrical components and operating procedures by challenging these systems to realistic operating conditions and train operational staff.

### Run systems through all sequences of operation and verify response of components.

### Notwithstanding all-inclusive requirements specified in this section, additional separate commissioning may be required at a later date for equipment and systems whose full operation is dependent on seasonal conditions.  Job conditions for Peak Performance Verification are as follows:

#### Summer sequence commissioning to take place between June 1st and September 15th when outside ambient temperatures are at least 22°C;

#### Winter sequence commissioning to take place between November 1st and March 31st when outside ambient temperature is no greater than minus 10°C.

### Carry out Cx:

#### Under actual operating conditions, over entire operating range, in all modes.

#### On independent systems and interacting systems.

### Cx procedures to be repeatable and reported results are to be verifiable.

### Follow equipment manufacturer's operating instructions.

### EMCS trending to be available as supporting documentation for performance verification.

### Contractor to obtain all documentation, including updated points list, controls sequences and setpoints, and submit documentation to commissioning authority for review. At completion of commissioning, scan completed manuals to electronic format on CD(s) in PDF format as required and submit to CxA.

## WITNESSING COMMISSIONING

### CxA along with designated representatives to witness activities and verify results.

## AUTHORITIES HAVING JURISDICTION

### Where specified start-up, testing or commissioning procedures duplicate verification requirements of authority having jurisdiction, arrange for authority to witness procedures so as to avoid duplication of tests and to facilitate expedient acceptance of facility.

### If the CxA is not available to witness, the certificates of approval from the Authority Having Jurisdiction will be accepted as adequate.

### Obtain certificates of approval, acceptance and compliance with rules and regulation of authority having jurisdiction.

### Provide copies to CxA within five (5) working days of test and with Cx report.

## REPEAT VERIFICATIONS

### Assume costs incurred by Owner’s Commissioning representatives for second and subsequent verifications where:

#### Verification of reported results fails to receive CxA's approval.

#### Repetition of second verification again fails to receive approval.

#### CxA deems Contractor's request for second verification was premature.

## DEFICIENCIES, FAULTS, DEFECTS

### Report problems, faults or defects affecting Cx to the Owner in writing. Stop Cx until problems are rectified. Proceed with written approval from CxA.

### Correct deficiencies found during start-up and Cx to satisfaction of CxA.

## COMPLETION OF COMMISSIONING

### Upon completion of Cx leave systems in normal operating mode.

### Except for warranty and seasonal verification activities, complete Cx prior to application for Substantial Completion.

### Cx to be considered complete when all Cx deliverables have been submitted and accepted by CxA.

### The CxA is to compile a Final Commissioning Report summarizing all tasks, findings and documentation of the commissioning process. The Final Commissioning Report is to incorporate all test reports by sub-contractors, manufacturer’s and controlling authorities including the following list.  The Contractor shall turn over all materials per this specification.

#### Evaluation of operating condition of the systems at the time of functional test completion.

#### Deficiencies that were discovered and measures taken to correct them.

#### Functional test procedures and results.

#### Documentation of all commissioning field activities as they progressed.

#### Description and estimated schedule of required deferred testing.

### The Contractor to provide O&M manuals, maintenance materials, warranties and training records.

## ACTIVITIES UPON COMPLETION OF COMMISSIONING

### When changes are made to baseline components or system settings established during Cx process notify the CxA. The CxA will update and provide Cx forms for affected item.

## TRAINING

### In accordance with Section 01 79 00.13 – Demonstration and Training for Building Commissioning, the Cx Manual and respective technical sections.

## MAINTENANCE MATERIALS, SPARE PARTS, SPECIAL TOOLS

### Supply, deliver, and document maintenance materials, spare parts, and special tools as specified in contract. Provide transmittal documenting all materials provided.

## OCCUPANCY

### Cooperate fully with CxA during stages of acceptance and occupancy of facility.

## PERFORMANCE VERIFICATION TOLERANCES

### Application tolerances:

#### Specified range of acceptable deviations of measured values from specified values or specified design criteria, except for special areas, to be within +/- 5 % of specified values.

### Instrument accuracy tolerances:

#### To be of higher order of magnitude than equipment or system being tested.

### Measurement tolerances during verification:

#### Unless otherwise identified, recorded values to be within +/- 2 % of specified values.

## OWNER'S PERFORMANCE TESTING

### Performance testing of equipment or system by CxA will not relieve Contractor from compliance with specified start-up and testing procedures.

# PRODUCTS (NOT APPLICABLE)

# EXECUTION

## SCHEDULE

### Provide a detailed schedule as per this section for on-site verification activities by the commissioning team based on the Cx Manual provided by the CxA. Be responsible for resource allocation respecting the exact number and duration for personnel required to perform the tasks required.

### This schedule shall be submitted with the general construction schedule monthly. The level of detail shall increase as the construction progresses.

## COMMISSIONING TASKS

### Refer to the Cx Manual provided by the CxA for a list of tasks to be conducted for the commissioning process. Further specifics are provided within applicable specification sections.

### END OF SECTION