# General

## Section Includes

### Commissioning forms to be completed for equipment, systems and integrated systems.

## Related Sections

### Section 01 78 00 – Closeout Submittals.

### Section 01 79 00.13 – Demonstration and Training for Building Commissioning.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

## INSTALLATION VERIFICATION CHECK LISTS

### Prior to initiation of Performance Verification the CxA will develop and provide to the contractor the required project specific Cx Manual which will include the Installation Verification check lists.

### Completed Installation Verification Checklists to be submitted to CxA for review and approval.

### Include the following data:

#### Product manufacturer's installation instructions and recommended checks.

#### Special procedures as specified in relevant technical sections.

#### Items considered good installation and engineering industry practices deemed appropriate for proper and efficient operation.

### Equipment manufacturer's installation/start-up check lists are acceptable for use in conjunction with installation verification check lists forming part of the Cx manual. Manufacturer’s check sheets used must be attached to final document submittals.

### Installer to sign check lists upon completion, certifying stated checks and inspections have been performed. Completed check lists to be submitted by the contractor at completion of the Commissioning Process.

### Use of check lists will be considered part of commissioning process.

## PERFORMANCE VERIFICATION CHECK LISTS

### The CxA will develop and provide to the Contractor the required project specific Cx Manual including the Performance Verification check lists.

### Completed Performance Verification Checklists to be submitted to CxA for review and approval.

### Strategy for Use:

#### Contractor will provide required shop drawings information and verify correct installation and operation of items indicated on these forms.

#### Confirm operation as per design criteria and intent.

#### Identify variances between design and operation and reasons for variances.

#### Verify operation in specified normal and emergency modes and under specified load conditions.

#### Record analytical and substantiating data.

#### Verify reported results.

#### Form to bear signatures of recording technician and reviewed and signed off by General Contractor, Installing Contractor, Consultant, DTI Representative, and the Commissioning Agent.

#### Reported results in true measured SI (metric) unit values.

#### Maintain copy on site during start-up, testing and commissioning period.

#### Forms to be both hard copy and electronic format.

#### .4	Upon completion of Performance Verification the contractor shall submit all completed checklists to the CxA.

#### .5	Final submittal shall include all Installation Verification, Performance Verification check lists, training records, maintenance materials transmittals, written warranties and a list of all Cx activities postponed due to seasonal, climatic, occupancy, or other reasons beyond the contractor’s control.

# Products (not applicable)

# Execution (not applicable)

END OF SECTION