# GENERAL

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 45 00 - Quality Control.

### Section 03 20 00 - Concrete Reinforcing.

### Section 03 33 00 - Cast-in-Place Concrete.

## REFERENCES

### American Society for Testing and Materials (ASTM)

#### ASTM C873/C873M, Standard Test method for Compressive Strength of Concrete Cylinders Cast in Place in Cylindrical Molds.

### Canadian Standards Association (CSA)

#### CSA-A23.1/A23.2, Concrete Materials and Methods of Concrete Construction/Methods of Test and Standard Practices for Concrete.

#### CSA A283, Qualification Code for Concrete Testing Laboratories.

## SUBMITTALS

### Provide inspection reports in accordance with Section 01 33 00 – Submittal Procedures.

### Submit testing results and reports for review by Owner and do not proceed without written approval when deviations from mix design or parameters are found.

### Prepare and submit certified written reports that include the following, except where otherwise specified:

#### Date of issue.

#### Project title and number.

#### Name, address, and telephone number of testing agency

#### Date, time, batch ticket number, and location of samples and tests or inspections.

#### Names of individuals making tests and inspections.

#### Description of the Work and test and inspection method.

#### Identification of product and Specification section.

#### Complete test or inspection data.

#### Test and inspection results and an interpretation of test results.

#### Ambient conditions at time of sample taking and testing and inspecting.

#### Comments or professional opinion on whether tested or inspected Work complies with the Contract Document requirements.

#### Recommendations on re-testing and re-inspecting.

### Submit material test reports at regular intervals mutually agreed upon between the testing agency and the Owner, but no later than five (5) working days after completion of the test.

### Upon completion of the Work requiring concrete inspection and testing, submit a final report summarizing previous reports, signed by the agency’s inspector responsible for the testing and inspection program.

### Submit copies of reports to the following:

#### Contractor.

#### Concrete Supplier.

#### Owner.

## QUALITY ASSURANCE

### All tests and test results shall be calculated, recorded and submitted on industry standard worksheets.

### All inspection reports and test results worksheets shall be signed and certified for correctness by the inspector or individual that carried out the test, respectively.

### All test and test result worksheets shall be reviewed and certified for correctness by a Professional Engineer employed by the Testing and Inspection firm, on a minimum weekly basis.

### Review and provide comments and recommendations regarding the Contractor’s mix designs when requested by the Owner.

### Notify the Owner of noncompliant, or potentially noncompliant, workmanship or materials as soon as possible, but in any case, within one (1) day of discovery.

### Qualifications: Provide proof of qualifications when requested by Consultant.

#### Concrete testing laboratory and personnel shall be certified in accordance with CSA A283.

#### Inspection and testing agency shall be experienced in all aspects of the required work described in this Section and as required by certification agency.

#### Inspection and testing agency shall be independent of the Contractor.

## TESTING AGENCY

### The Owner may hire a CSA-approved Testing Agency who shall test concrete, reinforcement, and grout in accordance with CSA-A23.1/A23.2, and Section 01 45 00 – Quality Control.

### Pay for costs of tests of initial mix designs as specified from Cash Allowance.

### Testing paid for by the Contractor shall include:

#### Costs of retesting due to deficient work or where tests have failed to meet the specified requirements.

#### Review of Contractor requested changes in materials or concrete mix design.

#### Any waiting time incurred by the Testing Agency in excess of thirty (30) minutes.

#### Any additional costs due to overtime, shift work, holiday or weekend work, except that the Owner will pay for holiday or weekend pickup when the concrete was placed on a regular workday.

#### Costs for testing required by the Contractor for stripping of formwork, such as field cure cylinders etc.

## RESPONSIBILITY OF THE CONTRACTOR

### Cooperate fully with the Owner’s appointed Testing Agency.  This includes providing access to the project site or to source of materials and assisting the Testing Agency in obtaining and handling samples at project site or at source of materials.

### Submit for review the concrete supplier’s quality control program to the Owner.

### Advise the Testing Agency at least twenty-four (24) hours in advance of a concrete placement to allow for scheduling of quality assurance tests, review of project requirements, and assignment of personnel.

### Provide a finished product that meets the specification. If initial tests indicate that the concrete failed to meet the specification, additional testing is necessary. This testing shall be done by a CSA-approved Testing Agency, but need not be the Owner’s agency.

### Core strengths must equal the specified strength if tested dry or 85% of specified if tested wet, with wet or dry tests as per the Standard.

## RESPONSIBILITY AND DUTIES OF THE TESTING AGENCY APPOINTED BY THE OWNER

### Responsible to the Owner and has the authority to, and is expected to reject any concrete not conforming to the Contract Documents.

### Inspect, sample, and test materials and concrete production as required. If material furnished or Work performed by the Contractor fails to conform to the Contract Documents, the testing agency will report deficiency to the Owner, Contractor and concrete supplier.

### If the Testing Agency becomes aware that concrete is being placed without their notification, or if insufficient notice is received, then the Testing Agency shall notify the Owner immediately.

### Low 7-day, 28-day and 56-day strength tests shall be brought immediately to the attention of the Owner.

## FIELD QUALITY CONTROL

### Inspection and testing of concrete and concrete materials will be carried out by a Testing Laboratory designated by Owner in accordance with CSA-A23.1/A23.2, and Section 01 45 00 - Quality Control.

### For compressive strength testing of concrete a minimum of four (4) cylinders and three (3) field cured cylinders are required for:

#### Each day’s pour.

#### Each type of grade of concrete.

#### Each change of supplier.

#### Each 50 cubic meters or fraction thereof for footings and foundation walls, requirements of CAN/CSA A23.1.

#### Conduct at least one (1) slump and one (1) air entrainment test with each compressive strength test.

### Take additional test cylinders during cold weather concreting. Cure cylinders on job site under same conditions as concrete which they represent.

### Non-destructive Methods for Testing Concrete shall be in accordance with CSA-A23.1/A23.2.

### Provide Certificate of Field Quality Inspection and Testing to Owner for inclusion in Commissioning Manual.

### Inspection or testing by Owner will not augment or replace Contractor quality control nor relieve the Contractor of his contractual responsibility.

## REPORTS

### Cylinder Testing:

#### All strength tests shall be numbered consecutively and cylinders marked as follows:

##### Seven (7) Day Test: Marked “A”.

##### 28 Day Test: Two (2) cylinders marked “B” and “C”.

##### 56 Day Test: Where these are required by the drawings and specifications, two (2) cylinders marked “D” and “E”.

##### Labelled with the suffix “L” for laboratory cured and “F” for field cured cylinders.

#### Report test results of one (1) batch per form.

#### Include the following information for each report:

##### Project Name and Number, Contractor, and Subcontractor.

##### Concrete Supplier.

##### Date and time of sampling.

##### Air temperature at time of sampling.

##### Concrete Mix Design Identification.

##### Exact location on the structure where concrete is being placed.

##### Specimen Number.

##### Concrete Temperature.

##### Specified concrete strength.

##### Specified slump.

##### Slump, measured at point of discharge from the delivery vehicle, prior to addition of plasticizing agent.

##### Specified air content.

##### Measured air content.

##### Method of curing.

##### Test number.

##### Test date and age of cylinder.

##### Cylinder strength.

##### Running average of three consecutive strength tests as defined by A23.1 for the class of concrete being tested.

##### Remarks regarding compliance.

#### Store a carton of 12 cylinder moulds together with slump apparatus on site for use should a test be required when testing company inspector is not present; instruct Contractor on use of moulds and slump apparatus.

### Analysis of Concrete Production:

#### Submit to the Owner a summary table and associated strip charts for all classes of structural concrete placed on projects with 25 or more compressive strength tests.

#### Summary tables are to indicate at least the following information:

##### Classification of Concrete.

##### Project name.

##### Test number.

##### Compressive strength of concrete.

##### Supplier’s ticket number.

##### Date concrete placed.

##### Time batched.

##### Time tested.

##### Slump.

##### Air entrainment.

##### One (1) 7 day and two (2) 28 day compressive strength test results for each test.

##### Average strength and within test variation for the two (2) 28 day concrete test results for each test.

##### Moving average of three (3) consecutive 28 day concrete test results.

##### Average and standard deviation of 28 day concrete test results and an evaluation of conformance to CSA production guidelines.

#### Charts shall plot concrete slump, air content, individual compressive strength tests, and the moving average of three (3) consecutive compressive strength tests.

#### Tables and charts for each type or class of concrete are to be provided on a monthly basis for concrete supplied for the structure until completion of the concrete work.

#### When 56-day concrete testing is permitted by the Owner, summary charts and tables shall be provided for concrete tested at 56 days.

## INSPECTIONS

### Batch Plant and Truck Mixers

#### Make occasional reviews of the concrete batching facility for inspection and reporting of the following:

##### Storage of materials.

##### Batching equipment and operation.

##### Condition and operation of truck mixers.

### Fresh Concrete at Site

#### Review delivery slips for appropriate mix for application and time expired between batching and beginning of placing the load.

#### Addition of water to truck mixers after leaving the plant is governed by the limitations of CSA A23.1; notify the Contractor and Owner about concrete that has had water added.

#### Fresh concrete will be considered deficient for the following reasons:

##### Allowable time from mixing has been exceeded.

##### Water has been added beyond the limits of CSA A23.1.

##### Measured slump not within limits specified in mix design.

##### Measured air content not within limits specified for mix design.

##### Incorrect mix design for scheduled placement.

#### Notify the Contractor and Owner verbally and follow up with a written report about concrete that is considered deficient and should not be placed.

#### Notify the Owner verbally and follow up with a written report about placed concrete considered deficient.

#### Attend occasional site meetings as directed by the Owner to review inspection reports regarding quality control of concrete as it relates to: mixing, delivery, conveying, depositing, consolidation, curing, installation and removal of formwork, re-shoring and protection.

## TESTING

### General

#### Inspection and testing agency shall coordinate with the Contractor for notification requirements regarding the timing of testing and inspections.

#### Inspection and testing agency shall coordinate their activities with the Contractor; be aware of the current work schedule and bring to the attention of the Owner any testing or inspection requirement apparently being overlooked.

#### Additional tests may be directed by the Owner, or requested by the Contractor with reference to accelerated strength prediction, cold weather concreting and removal of forms:

##### Costs of tests requested by the Owner will be paid for by the Owner.

##### Costs of tests requested by the Contractor will be paid for by the Contractor.

#### Immediately inform the Owner where sufficient number of site visits is not clearly identified and make a recommendation for additional site visits as required to form an opinion as to the compliance of the work.

#### Immediately inform the Owner where site conditions are such that a reduced program of testing and inspection is deemed appropriate to form an opinion as to the compliance of the work.

#### Re-Testing/Re-Inspecting:

##### Provide quality control services, including re-testing and re-inspecting for construction that revised or replaced Work that failed to comply with requirements established by the Contract Documents.

##### Payment for costs arising from re-testing and re-inspection are the responsibility of the Contractor.

### Concrete – Regular

#### Perform a complete test set for each 50 m3 of concrete or 500 m2 of surface area of slabs or walls, or fraction thereof, and in any event, not less than one test set for each type of concrete each day it is used.

#### Each test set shall consist of a slump test, air content test, temperature measurement, and not less than four (4) cylinders for compression testing, all in accordance with CSA A23.2-3C and as follows:

##### Test one (1) cylinder at seven (7) days, moist cured.

##### Test two (2) cylinders at twenty-eight (28) days.

##### Test two (2) additional cylinders at fifty-six (56) if and when directed by Owner.

##### Contractor may elect to have testing agency make and test additional specimens at other ages to assist in determining timing of formwork removal; costs of this additional testing shall be borne by Contractor.

#### Testing for concrete with SCM’s to reduce the cement content  to conform to CSA A23.2, except each test shall consist of four (4) cylinders – one (1) for 7-day strength, one (1) for 28-day strength, and two (2) for 56-day strength.

#### For suspended structural floor slabs make two additional specimens for compression testing when the air temperature is below 0°C within 24 hours after a placement; additional specimens shall be standard concrete cylinders or concrete cylinders cast in place in cylindrical moulds and as follows:

##### Site cure cylinders in a manner that simulates as closely as possible to the curing of the concrete sampled.

##### Test cylinders prior to falsework removal.

##### Test specimens cast-in-place in cylindrical moulds in accordance with ASTM C873/C873M.

#### Field cure cylinders shall be stored on the floor right below the slab they represent and be protected against wind unless the floor below is heated, in which case they shall be stored on top of the slab but covered with a plywood box.  The cylinders are to be undisturbed at this location until picked up by the Testing Agency.

#### Chlorine ion tests shall be performed on the first set of compressive test cylinders taken from the first pour and the first post-tensioned slab pour, to show that the chloride ion content of these mixes satisfies the limits set out in CAN/CSA A23.1.

#### Conduct additional tests for air content as required by CSA A23.2-4C or CSA A23.2-7C.

#### Core tests, if required, shall be tested saturated, surface dry in accordance with CSA A23.1/A23.2; if core is taken from concrete that will remain dry during the life of the structure, the cores shall be tested air dry.

#### Provide Contractor with criteria for maintaining facilities for temporary storage of concrete test cylinders, review site curing of test cylinders and provide guidance to the Contractor regarding curing and storage procedures.

### Concrete – Full Time

#### Full time testing shall apply to:

##### Concrete above 40 MPa specified strength.

##### Parking slab concrete in suspended slabs.

#### Conform to CSA A23.2 and regular testing except:

##### The Testing Agency shall have a representative on the job site at all times that the concrete requiring full time testing is being placed.

##### Test the slump and air content from every truck and reject any concrete not within specification.

### Mass Concrete

#### Site testing for mass concrete is to be as above for concrete in general, plus temperature monitoring as below.

#### Install and monitor temperature measuring devices within mass concrete elements as follows:

##### Measuring devices shall be placed in each concrete pour where concrete thickness is 1000 mm or greater; provide devices in pairs, with a minimum of two (2) devices per 30 m3 of concrete in the mass concrete element.

##### Devices shall be installed throughout thickness of mass concrete element.  Locate 50% of the devices per element at the centre of the mass, and 50% near the surface of the element.

##### Measuring devices shall be in accordance with Owner’s written acceptance of the testing agency’s proposed locations.

### Reinforcement

#### The Testing Agency shall, at start of the project, perform at least one (1) tensile and bend test for each bar size used on the project. Such testing shall comply with the applicable CSA documents. Further testing may be requested at the Owner’s discretion.

#### The Testing Agency will select the bars to be tested from the reinforcing supplied to the construction site, not from the suppliers’ yard. The Contractor shall cut the bars to the required length and replace the shortened bars without cost to the Owner.

#### The Contractor shall supply mill certificates of chemical analysis in accordance with CAN/CSA G30.18R and G30.18W when requested.

#### For epoxy coated reinforcing steel, the Testing Agency will visit the epoxy coating fabrication site, as required, to satisfy themselves that the fabrications and quality control process is in accordance with ASTM A775M.  They shall report their findings to the Owner.

#### When bar fabrication occurs at temperatures less than 16° Celsius, submit copies of bend tests indicating acceptability at the fabrication temperature.

## DEFECTIVE WORK

### Repairs and classification of unacceptable concrete to be in accordance with CAN/CSA-A23.1.

### Remove defective concrete and embedded debris and repair as directed by Owner.

### Remove to bare concrete curing compounds detrimental to application of specified finishes.

### Concrete to be supplied at the minimum strength requirement at 28 days. Tests indicating strengths lower than specified will necessitate further testing as required by the Owner. Cost for such testing to be at the Contractor’s expense. Should further tests confirm low values, the Owner has the right to require strengthening of the affected area or removal and replacing of the weak concrete all to the Contractor’s expense.

### Repair all shrinkage cracks in the completed slab-on-grade to remain exposed employing a suitable epoxy injection technique acceptable to Owner to completely seal all such cracks, all to the Contractor’s expense.

# PRODUCTS (NOT APPLICABLE)

# EXECUTION (NOT APPLICABLE)

END OF SECTION