# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 05 12 23 - Structural Steel for Buildings.

### Section 05 21 00 - Steel Joist Framing.

### Section 05 50 00 - Metal Fabrications.

### Section 07 92 00 - Joint Sealants.

### Section 09 91 13 - Exterior Painting.

### Section 09 91 23 - Interior Painting.

## REFERENCES

### Canadian Standards Association (CSA)

#### CSA C22.2 No.79, Cellular Metal and Cellular Concrete Floor Raceways and Fittings.

#### CAN/CSA-S16, Design of Steel Structures.

#### CSA-S136, North American Specification for the Design of Cold Formed Steel Structural Members.

#### CSA W47.1, Certification of Companies for Fusion Welding of Steel Structures.

#### CSA W55.3, Certification for Companies for Resistance Welding of Steel and Aluminum.

#### CSA W59, Welded Steel Construction, (Metal Arc Welding) Metric.

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-1.181, Ready-Mixed Organic Zinc-Rich Coating.

### American Society for Testing and Materials, (ASTM)

#### ASTM A653/A653M, Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

### Canadian Sheet Steel Building Institute (CSSBI)

#### CSSBI 10M, Standard for Steel Roof Deck.

#### CSSBI 12M, Standard for Composite Steel Deck.

## DESIGN REQUIREMENTS

### Design steel deck using limit states design in accordance with CSA  S136 and CSSBI 10M and CSSBI 12M.

### Steel deck and connections to steel framing to carry dead, live and other loads including lateral loads, diaphragm action, composite deck action, and uplift as indicated.

### Deflection under specified live load not to exceed 1/240 of span, except that when gypsum board ceilings are hung directly from deck, live load deflection not to exceed 1/360 of span.

### Where vibration effects are to be controlled as indicated, dynamic characteristics of decking system to be designed to be in accordance with CAN/CSA-S16.

## SHOP DRAWINGS

### Submit drawings stamped and signed by qualified professional Engineer registered or licensed in the Province of Newfoundland and Labrador, Canada.

### Submit design calculations if requested by Owner.

### Indicate deck plan, profile, dimensions, base steel thickness, metallic coating designation, connections to supports and spacings, projections, openings, reinforcement details and accessories.

# Products

## MATERIALS

### Zinc-iron Alloy (ZF) coated steel sheet: to ASTM A653/A653M structural quality Grade 230, 255, with ZF75 coating, for interior surfaces not exposed to weather, minimum base steel thickness as indicated on the drawings.

### Decks to be painted: zinc-iron alloy coated decks suitable for finish painting.

### Acoustic insulation: fibrous glass 17.5 kg/m3 density profiled to suit deck flutes.

### Closures: as indicated in accordance with manufacturer's recommendations.

### Cover plates, cell closures and flashings: steel sheet with minimum base steel thickness of 0.76 mm. Metallic coating same as deck material.

### Primer: zinc rich, ready mix to CAN/CGSB-1.181.

### Caulking: to Section 07 92 00 – Joint Sealants.

### Painting: to Section 09 91 23 – Interior Painting.

### Shear studs: to CSA W59.

## TYPES OF DECKING

### Steel roof deck: non-cellular , interlocking side laps.  Base steel thickness, depth & profile as shown on the drawings.

### Acoustic steel roof deck: non-cellular, perforated on vertical face of flutes, interlocking side lap, base steel thickness, depth & profile as shown on the drawings. Flat sheet for cellular deck, 0.76 mm minimum base steel thickness.

### Composite steel floor deck: non-cellular, upright embossed fluted profile, interlocking side lap, base steel thickness, depth & profile as shown on the drawings. Flat sheet for cellular deck, 0.76 mm minimum base steel thickness.

### Cellular roof deck for electrical raceway: to CSA C22.2No.79.

# Execution

## GENERAL

### Structural steel work: in accordance with CAN/CSA-S136 and CSSBI 10M and CSSBI 12M.

### Welding: in accordance with CSA W59, except where specified otherwise.

### Companies to be certified under Division 1 or 2.1 of CSA W47.1 for fusion welding of steel and/or CSA W55.3 for resistance welding.

## ERECTION

### Erect steel deck as indicated and in accordance with CSA S136 CSSBI 10M and CSSBI 12M and in accordance with approved reviewed erection drawings.

### For cellular deck butt ends: to 1.5 to 3 mm gap. Install steel cover plates over gaps wider than 3 mm.

### For non-cellular deck lap ends to 50 mm minimum.

### Weld and test stud shear connectors through steel deck to steel joists/beams below in accordance with CSA W59.

### Immediately after deck is permanently secured in place, touch up metallic coated top surface with compatible primer where burned by welding.

### Prior to concrete placement, steel deck to be free of soil, debris, standing water, loose mil scale and other foreign matter.

### Temporary shoring, if required, to be designed to support construction loads, wet concrete and other construction equipment. Do not remove temporary shoring until concrete attains 75% of its specified 28 day compression strength.

### Place and support reinforcing steel as indicated.

## CLOSURES

### Install closures in accordance with approved details.

## OPENINGS AND AREAS OF CONCENTRATED LOADS

### No reinforcement required for openings cut in deck which are smaller than 150 mm square.

### Frame deck openings with any one dimension between 150 to 300 mm as recommended by manufacturer, except as otherwise indicated.

### For deck openings with any one dimension greater than 300 mm and for areas of concentrated load, reinforce in accordance with structural framing details, except as otherwise indicated.

## CONNECTIONS

### Install connections in accordance with CSSBI recommendations as indicated on the drawings whichever is the most stringent.

## PROTECTION

### Protect installed products and components from damage during construction.

### Repair damage to adjacent materials caused by steel decking installation.

## FIELD TOUCH-UP PAINTING

### Upon erection completion, mechanically brush clean bolts, rivets, welds, and burned or scratched surfaces.

### For galvanized steel surface with damage and without shop coat, repair with field touch up primer.

END OF SECTION