# GENERAL

## RELATED SECTIONS

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 05 50 00 – Metal Fabrications.

### Section 06 10 53 – Miscellaneous Rough Carpentry.

### Section 07 62 00 – Sheet Metal Flashing and Trim.

### Section 07 92 00 – Joint Sealants.

## REFERENCES

### American Society for Testing and Materials (ASTM)

#### ASTM A 506, Specification for Alloy and Structural Alloy Steel, Sheet and Strip, Hot-Rolled and Cold-Rolled.

#### ASTM A 653/A 653M, Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

### Canadian Standards Association (CSA)

#### CSA B111, Wire Nails, Spikes and Staples.

### The Master Painters Institute (MPI)

#### Architectural Painting Specification Manual, MPI #76, Primer, Alkyd, Quick Dry, for Metal.

## DESIGN REQUIREMENTS

### Roof hatches to withstand local predominant snow loads, wind uplift and temperature range without damage to unit or permanent deformation to seals.

## SUBMITTALS

### Indicate size and description of components, materials, attachment devices, description of frame and finish, and construction details.

### Submit manufacturer's printed product literature, specifications and data sheet.

### Submit two copies of WHMIS MSDS - Material Safety Data Sheets. Indicate VOC's for caulking materials during application and curing.

### Submit manufacturer's installation instructions.

## CLOSEOUT SUBMITTALS

### Provide maintenance data for hardware complete with pertinent details, spare parts lists and warnings against harmful maintenance materials and practices for incorporation into manual specified in 01 78 00 - Closeout Submittals.

# PRODUCTS

## MATERIALS

### Steel sheet: regular quality alloy steel to ASTM A506.

### Galvanized steel sheet: commercial quality to ASTM A653, Z275 designation zinc coating.

### Aluminum sheet: mill finish plain utility sheet.

### Aluminum: extruded sections of AA6063-T5 alloy, all components one piece without splices.

### Gaskets: extruded resilient neoprene, with full recovery after 50% compression.

### Fasteners: screws to manufacturers’ standard cadmium plated steel galvanized steel stainless steel.

### Sealants: as per Section 07 92 00 – Joint Sealants.

### Prime paint for steel: to MPI #76.

### Isolation coating: alkali resistant bituminous paint or epoxy solution.

## HATCH COVER

### Metal Cover: Preformed, galvanized steel 2.0 mm overall thickness.

### 25 mm thick insulation to be fully covered and protected by a galvanized metal liner.

## CURBED FRAME

### Reformed metal curb: 2.0mm thick insulated sandwich construction, with deck flange for attachment.  Curb to be minimum 300 mm height above finished roof.

## ACCESSORIES

### Screws: galvanized steel for curb to structure and for hatch lip frame to outer attachment.

### Hinges: type recommended by roof hatch manufacturer of galvanized steel.

### Latch: positive snap with turn handles inside and out and padlock hasps inside.

### Securing latch: hold open operating arm with vinyl grip handle to permit one-handed release.

### Resilient gasket/seal to inner face of lid in contact with hatch lid support frame.

## FABRICATION

### Fabricate components free of twists, bends, or visual distortion and insulated. Weld corners and joints.

### Assemble roof hatch components as indicated.

### Ensure continuity of weather-tight seal.

### Design flashings extrusions to collect and lead off accumulated condensation.

### Zinc plate hardware and attachments and shop prime ready for field painting.

# EXECUTION

## INSTALLATION

### Erect components plumb, level and in proper alignment.

### Ensure continuity of building envelope air barrier and vapour retarder systems.

### Adjust and seal assembly with provision for expansion and contraction of components.

### Secure prefabricated curb assembly or brake formed metal curb to structure.

### Coat aluminum and copper in contact with dissimilar materials, with isolation coating.

### Secure and seal frame to curb.

## CLEANING

### Upon completion of installation, remove surplus materials, rubbish, tools and equipment barriers.

END OF SECTION