# GENERAL

## RELATED WORK

### Fire stopping and smoke seals within mechanical assemblies (i.e inside ducts, dampers) and electrical assemblies (i.e. inside cable trays) are specified in Division 23 and 26 respectively.

### Coordinate work of this section with other sections as required to properly execute the work and as necessary maintain satisfactory progress of the work of other sections.

## RELATED SECTIONS

### Section 01 33 00 – Submittal Procedures.

### Section 01 43 39 – Mock Up Requirements.

### Section 01 45 00 – Quality Control.

## REFERENCES

### Underwriter’s Laboratories of Canada (ULC)

#### CAN-S115, Fire Tests of Firestop Systems.

## DEFINITIONS

### Fire Stop Material: device intended to close off opening or penetration during fire or materials that fill openings in wall or floor assembly where penetration is by cables, cable trays, conduits, ducts and pipes and poke-through termination devices, including electrical outlet boxes along with their means of support through wall or floor openings.

### Single Component Fire Stop System: fire stop material that has Listed Systems Design and is used individually without use of high temperature insulation or other materials to create fire stop system.

### Multiple Component Fire Stop System: exact group of fire stop materials that are identified within Listed Systems Design to create on site fire stop system.

### Tightly Fitted; (ref: NBC Part 3.1.9.1.1 and 9.10.9.6.1): penetrating items that are cast in place in buildings of noncombustible construction or have "0" annular space in buildings of combustible construction.

#### Words "tightly fitted" should ensure that integrity of fire separation is such that it prevents passage of smoke and hot gases to unexposed side of fire separation.

## SUBMITTALS

### Prior to start of work submit the following:

#### Duplicate 300 x 300 mm samples showing actual firestop material proposed for project.

#### Shop drawings to show proposed material, reinforcement, anchorage, fastenings and method of installation. Construction details should accurately reflect actual job conditions.

#### Manufacturer’s engineering judgement identification number and drawing details when no ULC or cUL system is available. Engineering judgement must include both project name and contractor’s name who will install firestop system as described in drawing.

#### Manufacturer's product data for materials and prefabricated devices, providing descriptions are sufficient for identification at job site. Include manufacturer's printed instructions for installation. Include manufacturer’s specifications, training letter, and technical data for each material including the composition and limitations, documentation of ULC or CUL firestop systems to be used.

#### Material safety data sheets provided with product delivered to job site.

## MOCK-UP

### Construct mock-up in accordance with Section 01 43 39 – Mock Up Requirements.

### Construct mock-up showing service penetrations, fire separation and floor assemblies. Mock-up may be part of finished work.

## MANUFACTURER’S REPRESENTATIVE

### A manufacturer’s representative is to be on site during initial installation of firestop systems to train appropriate contractor personnel in proper selection and installation procedures and at commissioning stage to certify acceptance completed installation.  Training will be done as per manufacturer’s written recommendations published in their literature and drawing details.

## QUALITY ASSURANCE

### Qualifications:

#### Installer: person specializing in fire stopping installations with minimum five (5) years documented experience approved by the fire stopping manufacturer.

#### Manufacturer: company with minimum five (5) years experience in producing of material used for work required for this project, with sufficient production capacity to produce and deliver required units without causing delay in work.

### All fire stopping materials for this project to be supplied by a single manufacturer.

# PRODUCTS

## MATERIALS

### Use only firestop products that have been ULC or cUL tested for specific fire-rated construction conditions conforming to construction assembly type, penetrating item type, annular space requirements and fire-rating involved for each separate instance.

### Fire stopping and smoke seal systems: in accordance with CAN-S115.

#### Asbestos-free materials and systems capable of maintaining an effective barrier against flame, smoke and gases in compliance with requirements of CAN-S115 and not to exceed opening sizes for which they are intended.

#### Firestop system rating:  as indicated on drawings.

### Service penetration assemblies: certified and tested by ULC or cUL in accordance with CAN-S115.

### Service penetration firestop components: certified and tested by ULC or cUL in accordance with CAN-S115.

### Fire-resistance rating of installed fire stopping assembly in accordance with NBC.

### Non-curing, re-penetrable intumescent sealants, caulking or putty material for use with flexible cables or cable bundles.

### Fire stopping and smoke seals at openings around penetrations for pipes, ductwork and other mechanical items requiring sound and vibration control: elastomeric seal. Consult with Owner and damper manufacturer prior to installation ULC or cUL firestop systems that might hamper the performance of fire dampers as it pertains to duct work.

### Intumescent sealants or caulking materials for use with combustible items (penetrants consumed by high heat and flame) including insulated metal pipe, PVC jacketed, flexible cable or cable bundles and plastic pipe. No silicone based firestop are allowed to be applied on plastic pipes.

### Primers: to manufacturer's recommendation for specific material, substrate, and end use.

### Water (if applicable): potable, clean and free from injurious amounts of deleterious substances.

### Damming and backup materials, supports and anchoring devices: to manufacturer's recommendations, and in accordance with tested assembly being installed as acceptable to authorities having jurisdiction.

### Sealants for vertical joints: non-sagging.

# EXECUTION

## PREPARATION

### Examine sizes and conditions of voids to be filled to establish correct thicknesses and installation of materials. Ensure that substrates and surfaces are clean, dry and frost free.

### Prepare surfaces in contact with fire stopping materials and smoke seals to manufacturer's instructions.

### Maintain insulation around pipes and ducts penetrating fire separation without interruption to vapour barrier.

### Mask where necessary to avoid spillage and over coating onto adjoining surfaces; remove stains on adjacent surfaces.

## INSTALLATION

### Install fire stopping and smoke seal material and components in accordance with ULC certification or UL Products Certified for Canada (CUL) and manufacturer's instructions.

### Seal holes or voids made by through penetrations, poke-through termination devices, and unpenetrated openings or joints to ensure continuity and integrity of fire separation are maintained.

### Provide temporary forming as required and remove forming only after materials have gained sufficient strength and after initial curing.

### Tool or trowel exposed surfaces to a neat finish.

### Remove excess compound promptly as work progresses and upon completion.

## INSPECTION

### Notify Owner when ready for inspection and prior to concealing or enclosing firestopping materials and service penetration assemblies.

## SCHEDULE

### Firestop and smoke seal at:

#### Penetrations through fire-resistance rated masonry, concrete, and gypsum board partitions and walls.

#### Edge of floor slabs at curtain wall and precast concrete panels.

#### Perimeter of fire-resistance rated masonry and gypsum board partitions.

#### Intersection of fire-resistance rated masonry and gypsum board partitions.

#### Control and sway joints in fire-resistance rated masonry and gypsum board partitions and walls.

#### Penetrations through fire-resistance rated floor slabs, ceilings and roofs.

#### Openings and sleeves installed for future use through fire separations.

#### Around mechanical and electrical assemblies penetrating fire separations.

#### Rigid ducts: greater than 129 cm2: fire stopping to consist of bead of fire stopping material between retaining angle and fire separation and between retaining angle and duct, on each side of fire separation.

## FIRE SEPATATIONS

### Coordinate fire separation labelling/stenciling as per Sections 09 91 23 – Interior Painting and 09 01 90.63 – Interior Re-Painting.

## CLEAN UP

### Remove excess materials and debris and clean adjacent surfaces immediately after application.

### Remove temporary dams after initial set of fire stopping and smoke seal materials.

END OF SECTION