# GENERAL

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 05 50 00 - Metal Fabrications.

### Section 06 10 53 – Miscellaneous Rough Carpentry.

### Section 08 71 00 - Door Hardware.

### Section 09 91 23 - Interior Painting.

### Division 26 – Smoke detection connections

## REFERENCES

### Aluminum Association (AA).

#### DAF 45, Designation System for Aluminum Finishes.

### American Architectural Manufacturers Association (AAMA)

#### AAMA 609/610, Cleaning and Maintenance Guide for Architecturally Finished Aluminum.

### American Society for Testing and Materials International, (ASTM).

#### ASTM A167, Specification for Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet and Strip.

#### ASTM A276, Specification for Stainless and Heat-Resisting Steel Bars and Shapes.

#### ASTM A480/480M, Specification for General Requirements for Flat-Rolled Stainless and Heat-Resisting Steel Plate, Sheet and Strip.

### Canadian General Standards Board (CGSB).

#### CAN/CGSB 1.198, Cementitious Primer for Galvanized Surfaces.

#### CAN/CGSB-85.100, Painting.

### Canadian Standards Association (CSA).

#### CAN/CSA-O141, Softwood Lumber.

### National Fire Protection Association (NFPA).

#### NFPA 80, Standard for Fire Doors and Other Opening Protectives.

### Underwriters' Laboratories of Canada (ULC).

#### CAN4-S104, Standard Method for Fire Tests of Door Assemblies.

#### CAN/ULC-S105, Standard Specification for Fire Door Frames.

## SUBMITTALS

### Product Data:

#### Submit manufacturer's printed product literature, specifications and data sheet.

#### Submit two copies of WHMIS SDS – Safety Data Sheets. Indicate VOC’s:

##### For caulking materials during application and curing.

##### For door materials and adhesives.

### Shop Drawings:

#### Indicate each type of coiling counter door, arrangement of hardware, operating mechanism and required clearances.

### Submit duplicate 300mm long pieces of coiling curtain slats, guides frame.

### Manufacturer's Instructions:

#### Submit manufacturer's installation instructions.

### Submit copies of manufacturer’s field reports.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for overhead coiling counter doors and hardware for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## QUALITY ASSURANCE

### Steel fire rated doors and frames: labelled and listed by an organization accredited by Standards Council of Canada in conformance with CAN/ULC -S104 and CAN/ULC -S105 for ratings specified or indicated.

### Fabricate and install fire rated coiling metal counter doors in accordance with NFPA 80 to suit fire protection rating required.

## Warranty

### Provide a written guarantee, signed and issued in the name of the owner, covering the coiling counter doors for both material and workmanship for a period of 5 (five) years from the date of Substantial Completion.

### Areas which prove to be defective in any way shall be repaired or replaced and any damage to other work as a result of such defects shall be repaired at no cost to the Owner.

# PRODUCTS

## MATERIALS

### Galvanized steel sheet: commercial quality with Coating Designation Z275 mill phosphatized.

### Primer: to CAN/CGSB-85.100.

#### For galvanized sheet steel: CGSB 1-GP-198, primer cementitious (for galvanized surfaces).

### Curtain: roll formed galvanized steel.

## COILING COUNTER DOORS

### Fabricate fire rated rolling metal coiling counter doors to NFPA 80 with 3/4 hours fire rating.

### Rivet continuous end locks to slat ends.

### Assemble coiling counter door curtain of 45 mm x 13 mm thick, flat roll formed steel interlocking slat sections.

### Provide bottom bar of equal mass, steel angles.

### Form guides of metal angles of 5.0 mm minimum thickness for between jambs installation.

### Construct counterbalance assembly consisting of torsion spring with 25% overload factor. Enclose spring in steel pipe to support door curtain and counterbalance mechanism with maximum deflection of 1/360th of opening width. Provide ball bearings at rotating points. Provide spring tension adjusting wheel, accessible for setting.

### Support counterbalance assembly on 5.0 mm minimum thickness steel plate brackets, forming end enclosures.

### Enclose counter balance assembly with galvanized steel sheet formed hood.

### Attach to hood sheet metal flame and smoke baffle to drop in place automatically when activated by temperature rise and melting of fusible link.

### Equip coiling doors for locking from inside with slide bolts and padlocking.

## OPERATION

### Equip coiling counter doors for operation by:

#### Hand, install two lift handles at coiling counter door bottom on inside, outside face of coiling counter door or provide continuous extruded lifting strip.

### Install fusible link activated automatic closing device to cause door to close at controlled slow even speed in case of fire.

### Connect automatic closing device to smoke detection equipment.

# EXECUTION

## INSTALLATION

### Install coiling counter door in accordance with manufacturers' printed instructions.

### Adjust operable parts for correct function and smooth operation.

### Test labelled coiling counter doors for proper operation by activating fusible link. Test shutters in presence of Owner.

## CLEANING

### Perform cleaning of aluminum components in accordance with AAMA 609/610.

### Perform cleaning after installation to remove construction and accumulated environmental dirt.

### Clean aluminum with damp rag and approved non-abrasive cleaner in accordance with manufacturer’s instructions.

### Remove traces of primer, caulking; clean doors and frames.

### Upon completion of installation remove surplus materials, rubbish, tools and equipment barriers.

## COMMISSIONING

### Contractor to instruct maintenance personnel in operation and maintenance of doors and hardware.

### Confirm operation and function for all doors and hardware.

### Commissioning will be witnessed by Owner and certificate will be signed by Contractor and Owner.

END OF SECTION