# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 – Closeout Submittals.

### Section 23 05 17 – Pipe Welding.

### Section 23 08 01 – Performance Verification of Mechanical Piping Systems.

### Section 23 08 02 – Cleaning and Start-Up of Mechanical Piping Systems

## REFERENCES

### American Society of Mechanical Engineers (ASME)

#### ASME Boiler and Pressure Vessel Code Section VIII Pressure Vessels.

#### ASME B16.5, Pipe Flanges and Flanged Fittings.

#### ASME B16.11, Forged Fittings, Socket-Welding and Threaded.

### American Society for Testing and Materials (ASTM)

#### ASTM A 53/A53M, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless.

#### ASTM A 181/181M, Specification for Carbon Steel Forgings for General Purpose Piping.

### Canadian Standards Association (CSA)

#### CSA B51, Boiler, Pressure Vessel, and Pressure Piping Code.

## shop drawings and product data

### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

## CLOSEOUT SUBMITTALS

### Provide maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

# Products

## air compressor

### General:

#### Frame:  100% cast iron frame.  Cylinders bolt directly to the cast iron frame.  Frame is completely sealed yet allows for maximum accessibility.

#### Crankshaft:  Overhung design supported by two heavy duty ball bearings with replaceable crankpin bushing.  Entire shaft is balanced with an integral counterweight to ensure smooth operation.

#### Connecting rods:  Solid one-piece design.  Crankpin bushing inside the rod is precision ground requiring no alignment.

#### Cylinders:  100% cast iron, separately cast and individually bolted to the frame in a V-type configuration.  Radial fins on the cylinders help remove heat and ensure 360 degree cooling of the cylinders.

#### Pistons:  Precision balanced low pressure aluminum and high pressure cast iron pistons provide smooth operation.

#### Rings:  There are four piston rings for sealing compression and oil control.

#### Flywheel:  The cast iron fan type flywheel forces a “cyclone” air blast to provide cooling for the deep finned cylinders and multi-finned copper tub intercooler.  The flywheel is balanced to keep vibration to a minimum.

#### Intercooler:  Two stage compressors use an intercooler.  The intercooler between stages is of finned copper tube construction to provide maximum cooling area.  The intercooler is provided with a relief valve to prevent over-pressurization.

#### Lubrication:  Splash lubrication of running parts is simple and reliable.  Lubrication dippers are integral with connecting rods and cannot come loose.

#### Inlet filter:  The filter has a durable canister with a dry type 10 micron inlet filter/silencer.

#### Valves:  Inlet valves consist of finger valves which allow maximum air flow. Discharge valves are large bore ring valves.  Valve plate is easily removed for maintenance.

#### Oil Sight Glass:  Indicates visible oil levels at all times.

#### Base:  The compressor and motor are aligned on a heavy steel base.

#### Receiver:  Receiver mounted units are ASME, National Board coded, and include pressure gauge, drain valve, service valve and relief valve.

#### Drive:  The drive is V-belt type with provision for easy adjustment of belt slack.  An easily removed, totally enclosed beltguard is standard equipment.

#### Motor:  11.9 kW, 600/3/60 AC motors are 1800 rpm NEMA T frame with drip-proof enclosure, Class B insulation, 1.15 Service Factor, and grease lubricated ball bearings.  Standard three phase motor voltages are 200, 230/460 and 575.

#### Controls:  Automatic start and stop operation with NEMA 1 unloading pressure switch.

### Automatic start/stop with unloading pressure switch.  15 HP Simplex “Value Fully Packaged” E-Series starter, mounted and wired, in a NEMA-1 enclosure.  These packages also include an air-cooled aftercooler which removes up to 70% of the moisture in the compressed air.  Package features a totally enclosed belt guard, belt guard mounted air-cooled aftercooler, with electric (115-volt) automatic tank drain.  Install kit and start-up kit. U.L. and CSA approved.

## piping

### Piping to ASTM A53/A53M, schedule 80 seamless black steel.

### Fittings:

#### NPS2 and smaller:  to ASME B16.11, schedule 80 steel, socket welded.

#### NPS2 ½ and larger:  to ASME B16.11, schedule 80 steel, butt or socket welded.

### Couplings:  to ASME B16.11, socket welded or threaded half coupling type.

### Unions:  1000 kPa malleable iron with brass-to-iron ground seat.

### Dissimiliar metal junctions:  use dielectric unions.

### Flanges:

#### NPS2 and smaller:  to ASME B16.5, forged steel, raised face and socket welded.

#### NPS2 ½ and larger:  to ASME B16.5, forged steel, raised face and slip-on or weld neck.

### Joints:

#### NPS2 and smaller:  socket welded.

#### NPS2 ½ and larger:  butt welded.

## BALL VALVES

### Three piece design or top entry for ease of in-line maintenance.

#### To ASTM A181/A181M, Class 70, carbon steel body socket welded or screwed ends, carbon steel ball and associated trim suitable for compressed air application.

#### To withstand 1034 kPa maximum pressure.

## COUPLERS/CONNECTORS

### Industrial interchange series, full-bore.

### Maximum inlet pressure:  1700 kPa.

### Valve seat:  moulded nylon.

### Body:  zinc plated steel.

### Threads:  NPT

## COMBINATION FILTER-REGULATOR-LUBRICATOR GAUGE

### General:

#### 13 mm filter-regulator-lubricator.

#### 1205 kPa max.

#### 51.9 L/s max.

#### 40 micron.

#### 17 ml bowl size.

# Execution

## compressor station

### Install on vibration isolators on housekeeping pad as indicated.

## compressed air line filter

### Install on discharge line from refrigerated air dryer.

## MAIN AIR PRESSURE REGULATORS

### Install at air compressor station.

### Install additional regulators on connections to equipment as indicated.

## COMPRESSED AIR PIPING CONNECTIONS AND INSTALLATION

### Install flexible connection in accordance with Section 23 05 16 – Expansion Fittings and Loops for HVAC Piping.

### Install shut-off valves at outlets, major branch lines and elsewhere where indicated.

### Install quick-coupler chucks and pressure gauges on drop pipes.

### Install unions to permit removal or replacement of equipment.

### Install tees in lieu of elbows at changes in direction of piping.  Install plug in open ends of tees.

### Grade piping at 1% slope minimum.

### Install compressed air trap and pressure equalizing pipe at moisture collecting points.  Drain pipe to nearest floor drain.

### Make branch connections from top of main.

### Install compressed air trap at bottom of risers and at low points in mains, piped to nearest drain.  Distance between drain points to be 30 m maximum.

### Cleaning:

#### Blow out piping to clean interior thoroughly of oil and foreign matter.

### Testing:

#### Pressure test for 4 h minimum, to 1100 kPa, with outlets closed and with compressor isolated from system.  Pressure drop not to exceed 10 kPa.

## START-UP AND PERFORMANCE VERIFICATION

### Refer to Section 23 08 02 – Cleaning and Start-Up of Mechanical Piping System and Section 23 08 01 – Performance Verification of Mechanical Piping System.

END OF SECTION