# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 23 31 13.02 – Metal Duct – High Pressure to 2500 Pa.

## REFERENCES

### NFPA (Fire) 91, Exhaust Systems for Air Conveying of Materials.

### Sheet Metal and Air Conditioning Contractors Association (SMACNA)

## shop drawings and product data

### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

#### Indicate the following:

##### Manufacturer’s description data.

##### Schematic diagram.

##### Reel installation mounting brackets.

##### Fan.

##### Hose reel.

##### Push button station.

##### Electrical details.

##### Wiring diagrams.

##### Air flow performance data.

## certification of ratings

### Catalogued or published ratings shall be those obtained from tests carried out by manufacturer or those ordered by him from independent testing agency signifying adherence to codes and standards.

## GENERAL

### All components for the vehicle exhaust hose reel system shall be of a single manufacturer.

# Products

## hose reel assembly

### General:

#### Hose:  10 m of 150 mm diameter flexible hose.

#### The hose reel shall be motor operated and shall be capable of unwinding and recoiling the hose from a remote operating station.

#### All electrical equipment necessary for operation shall be mounted on the hose reel assembly except for the remote operating station.

#### The hose reel motor shall be interlocked with an adjustable limit switch that stops the reel when the tubing has been fully extended or fully retracted.

### Construction:

#### Drum:

##### End constructed of composite, with integrated sprockets for the drive gear.

##### Shaft with ball bearings.

##### Cylinder made of aluminum/zinc plated sheet steel.

#### Limit switches, for hose coiling and uncoiling – integrated in drive unit.

#### Motor turns drum via a planetary gear and the drum end sprocket gear, ratio 174:1.

#### Relay for fan, controls circuits integrated in drive unit.

#### Electric drive motor.

#### Adjustable brackets make installation easy.

#### Reel framework, made of zinc-plated square steel tube.

#### Reel frame side, constructed of composite with integrated electric motor drive.

#### Arm with indicator, LEDs showing reel status.  With receiving eye for remote control.

#### Flexible connection hose to duct system, 150 mm dia.

#### Duct connection, 150 mm.

#### Swivel, 150 mm dia.

#### Hose adaptor, made of aluminum.  Connects hose to internal duct.

#### Hose guide aligns the hose to the right position during first turn on the drum.

### Electric Drive Unit.

#### 120/1/60 Power, 3 Amps.

#### 24V DC drive motor.

#### Electromagnetic brake.

#### Normal load:  150 – 200 W.

#### Maximum load:  240 W.

#### Overload:  300 W.

### Fan Terminals:

#### Potential free contact closes by signal to uncoil hose and opens by signal to coil hose.

#### Voltage output relay for 24V DC fan contactor coil.  Maximum load 5 VA.  (Contact opens and closes as above).

## Hose

### High temperature fabric for 3000C continuous use, 3500C intermediate use.

### Light weight, heavy duty construction.

### High resistance to diesel particles.

### 150 mm diameter, 10 m long.

## MANUAL VEHICLE NOZZLE

### Metal Construction.

### Zinc coated.

### 150 mm diameter.

### 2.1 kg weight.

### Spring loaded lid.

## PENDANT CONTROL UNIT

### Hose reel push button controller for motor drive.

### Pendant control and cable for mounting unit 20 m from hose reel.

### 3 button (up, down, on/off) controller wired directly to the hose reel assembly.  The up and down buttons shall be momentary push button type.

## FAN

### Construction:

#### 14 gauge blown housing.

#### Polyester epoxy galvanized sheet metal housing.

#### Round duct connection.

#### Centrifugal backward curved impeller.

### Motor:

#### 3 HP, TEFC, 208/3/60 motor.

#### Direct drive.

#### Continuous duty type exceeding IP54 protection standards.

### Provide fan complete with mounting bracket (wall or ceiling) and silencer.

# Execution

## installation

### Install in accordance with NFPA 91, and to manufacturer’s instructions.

### Follow ACGIH industrial ventilation details.

### Hose reel and fan shall be installed in accordance with the manufacturer’s recommendations.

### Install drain from low point in overhead ducts to floor drain.

### Make joints watertight and airtight when subjected to 2500 Pa pressure.

### Install duct supports to manufacturer’s recommendations.

### Coordinate the location of all components with the owner in the field.

## testing

### Test assembled and sealed ductwork from fan inlet to suction inlets under 2.5 kPa pressure for 30 min.  Leakage not to exceed 1% of design total air flow.

### Demonstrate the proper operation of the exhaust system to the satisfaction of the Engineer. This shall include operation in conjunction with the garage ventilation system.

END OF SECTION