# GENERAL

## RELATED WORK

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Division 26 - Electrical Services.

## REFERENCE STANDARDS

### Canadian Standards Association (CSA)

#### CAN/CSA-B355, Lifts for Persons with Physical Disabilities.

#### CSA C22.1, Canadian Electrical Code, Part 1, Safety Standard for Electrical Installation.

## SUBMITTALS

### Submit manufacturer’s printed product literature, specifications and data sheets.

### Include on layout drawings:

#### Platform: size, travel, skirts, bridge plates, removable safety posts and chains, access panels, cylinder, and cylinder support.

#### Reactions at points of support.

#### Weights of principal components.

#### Location of circuit breaker, or disconnect switch, light switch and feeder extension points in machine room.

#### Rating of drive motor and fused disconnect.

#### Each shop drawing submitted shall bear stamp of qualified professional engineer registered in the Province of Newfoundland and Labrador.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance date for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

### Include in maintenance data:

#### Parts catalogue giving complete list of repair and replacement parts with cuts and identifying numbers.

#### Legible schematic wiring diagrams covering electrical equipment as supplied and installed, including changes made in final work.

#### Lubrication chart.

## MAINTENANCE SERVICE

### Include complete maintenance of Stair Lift for a period of twelve (12) months from date of the Certificate of Substantial Completion.

### Regularly, systematically examine, clean, adjust and lubricate equipment, every 3 months, and one visit must be within 4 days of building occupancy.

### Repair or replace electrical and mechanical parts as required due to defect and normal wear and tear.

### Use only genuine standard parts produced by manufacturer of equipment.

### Perform work by competent personnel under supervision and in direct employ of Lift manufacturer or manufacturer’s licensed agent.

### Maintain locally adequate stock of parts for replacement or emergency purposes and provide qualified personnel to ensure fulfillment of this service without undue loss of time in reaching job site.

### Include call-back service due to breakdown or malfunction during twelve (12) month maintenance period at no additional cost to Owner.

## GUARANTEE

### Provide twelve (12) months maintenance service commencing from the date of Certificate of Substantial Performance.

### The complete unit shall carry a three (3) year guarantee in association with the General Conditions of the Contract to replace any part or parts as required at no cost to the owner.

## QUALITY ASSURANCE

### Manufacturer must be a company experienced in the manufacture of Stair Lifts and must produce evidence of at least five (5) similar installations of the type specified.

### Installer must be a contractor licensed by manufacturer to install equipment of this type and must produce evidence of at least five (5) similar installations completed in the last three (3) years.

# PRODUCTS

## DESCRIPTION OF SYSTEM

### Platform: 900 mm x 1200 mm deck complete with power-fold, power-ramp, sequentially operating power safety arms, and seat.

### Rated Load: 200 kg with a minimum 5 times safety factor.

### Deck and ramps to have a non-slip surface.

### Speed:  6 metres per minute.

### Guide Rail: steel, offset C-channel, 400 mm x 60 mm.

### Motor: 1 hp, 208 volt, 3 phase.

### Power Supply: 208 Volts, 3 Phase.

### Drive Cabinet: 1372 mm x 280 mm x 180 mm deep, located at top of system. Hand wheel for operating during power failure.

### Oversewed Safety: mechanical oversewed sensor and lock with electric drive protection and brake.

### Roller Chain: double roller chain meeting ANSI specification B.29.2.

### Electric Controls: 24 volt.

### Finish: baked powder paint, electrostatically applied.

### Stop stations:  top and bottom and as otherwise indicated on Drawings.

### Steel Support Posts for Guide Rail: 65 mm x 65 mm structural steel tubular posts secured to vertical wall and floor or stair threads.

# EXECUTION

## EXAMINATION

### Take critical site dimensions to ensure tolerances and clearances to other constructions have been maintained, and necessary adjustments are made to adapt work of this Section during its installation.

### Ensure anchors, services, and similar provisions, installed by others, are adequate to meet specified requirements, and make adjustments before installation.

### Do not proceed with work of this Section until conditions and work on which it depends are satisfactory with limitations of adjustment.

## INSTALLATION

### Install in accordance with manufacturers’ instructions and regulations in force.

## PROTECTION

### Provide protective coverings for finished surfaces.

## TOUCH-UP

### Upon completion, touch up and restore to new condition, damaged or defaced factory finished surfaces.

### Remove protective coverings and clean exposed surfaces after completion.

## FIELD QUALITY CONTROL

### Engage only specialized tradesmen employed and under direct supervision of Lift manufacturer.

### Ensure Lift operation is free of vibration and performs smoothly and quietly.

### Perform and meet tests required by CAN/CSA-B355 and local authorities.

### Furnish test and approval certificates issued by jurisdictional authorities.

### Provide two (2) weeks written notice of date and time of tests after satisfactory completion.

## COMMISSIONING

### Train user staff in operation and maintenance of equipment.

END OF SECTION