# PART 1 - GENERAL

## RELATED Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 01 78 00 – Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Division 26 - Electrical Services.

## REFERENCES

### American National Standards Institute (ANSI).

#### ANSI A17.1, Safety Code for Elevators and Escalators.

### Canadian Standards Association (CSA)

#### CSA C22.1, Canadian Electrical Code Part 1, Safety Standard for Electrical Installations.

#### CSA B355, Lifts for Persons with Physical Disabilities.

#### ASME A17.1/CSA B44, Safety Code for Elevators and Escalators (Bi-National Standard, with ASME A17.1).

## SUBMITTALS

### Indicate:

#### Pit: showing bumpers, edge angle, drain, bucket sump, cylinder sleeve, sloped floor, removable hand rails, waterproofing and truck bumpers.

#### Platform: size, travel, skirts, bridge plates, removable safety posts and chairs, access panels, non-rotatng device, cylinder, two post equalizer, and cylinder support.

#### Power units: space, size and location

#### Control station locations.

#### Location of disconnect switch and electric power requirements.

## CLOSEOUT SUBMITTALS

### Provide maintenance data for Platform Lift for incorporation into maintenance manual specified in Section 01 78 00 - Closeout Submittals.

### Include:

#### Description of platform lift systems, method of operation.

#### Manufacturer’s instructions covering maintenance requirements and parts catalogue giving complete list of repair and replacement parts with cuts and identifying number.

#### Legible schematic wiring diagrams covering electrical equipment as supplied and installed, including changes made in final work, with symbols listed corresponding to identify as markings or equipment.

## MAINTENANCE SERVICE

### Include complete maintenance of Platform Lift for a period of twelve (12) months from date of the Certificate of Substantial Performance.

### Regularly, systematically every three (3) months examine, clean, adjust and lubricate equipment.

### Repair or replace electrical and mechanical parts as required due to defect and normal wear and tear.

### Use only genuine standard parts produced by manufacturer of equipment.

### Perform work by competent personnel under supervision and in direct employ of Lift manufacturer or manufacturer’s licensed agent.

### Maintain locally adequate stock of parts for replacement or emergency purposes and provide qualified personnel to ensure fulfillment of this service without undue loss of time in reaching job site.

### Include call-back service due to breakdown or malfunction during twelve (12) maintenance period at no additional cost to Owner.

## SYSTEM DESCRIPTION

### Unit to be supported on retractable coasters to provide easy movement from one area to another, have a self contained screw drive unit, control system, electrical wiring and accessories.

## GUARANTEE

### Provide one (1) year guarantee to replace any part or parts as required at no cost to the Owner from date of Substantial Completion.

## QUALITY ASSURANCE

### Manufacturer must be a company experienced in the manufacture of Platform Lifts and must produce evidence of at least five (5) similar installations of the type specified.

### Installer must be a contractor licensed to install equipment of this type and must produce evidence of at least five (5) similar installations completed in the last three (3) years.

# PRODUCTS

## COMPONENTS

### Description of System:

Rated Load:			341 kg.

Normal Speed:		0.04 m/s

Platform Dimensions:	890mm wide x 1372mm long

Levels Served:		2

Travel Distance:		1219 mm

Operation:			Constant Pressure

Power Supply:		110 Volts, 1 Phase, 15 Amps

Drive Type:			Acme Screw

### Lift Platform (car)

#### Frame and side guard panels:

##### Aluminum platform frame 1073 mm high with steel insert.

#### Floor:

##### Formed steel with anti-slip sheeting.

#### Grab rail:

##### A single grab rail with both ends returned to the wall shall be located on the control wall of the carriage.

#### Car operating panel:

##### Shall consist of constant pressure illuminated buttons, an emergency stop and alarm button, and an ON/OFF key switch mounted on a removable stainless steel panel (type 304 #4 stainless steel finish).

### Drive Unit and Controls:

#### The drive unit and controller shall be enclosed in the mast. The controller and drive unit shall be pre-wired and tested before shipment. Control circuitry is to be PCB mounted as an integral unit.

### Acme Screw:

#### 25 mm O.D., Class 2G, 5 pitch. Self lubricating nut and screw drive.

### Safety Device:

#### Integral Back up Safety Nut. In the event of failure of the main drive nut, the Back up Safety Nut will engage and trip a switch to stop the platform automatically.

### Emergency Manual Lowering:

#### The top of the Acme Screw must be accessible and equipped such that the screw may be turned by using a hand crank to lower the platform.

# EXECUTION

## EXAMINATION

### Take critical site dimensions to ensure tolerances and clearances to other constructions have been maintained, and necessary adjustments are made to adapt work of this Section during its installation.

### Ensure anchors, services, and similar provisions, installed by others, are adequate to meet specified requirements, and make adjustments before installation.

### Do not proceed with work of this Section until conditions and work on which it depends are satisfactory with limitations of adjustment.

## INSTALLATION

### Install in accordance with manufacturer’s instructions and regulations in force.

## PROTECTION

### Provide protective coverings for finished surfaces.

## TOUCH-UP

### Upon completion, touch up and restore to new condition, damaged or defaced factory finished surfaces.

### Remove protective coverings and clean exposed surfaces after completion.

## FIELD QUALITY CONTROL

### Engage only specialized tradesmen employed and under direct supervision of Lift manufacturer.

### Ensure Lift operation is free of vibration and performs smoothly and quietly.

### Perform and meet tests required by CAN/CSA-B355 and local authorities.

### Furnish test and approval certificates issued by jurisdictional authorities.

### Provide two (2) weeks written notice of date and time of tests after satisfactory completion.

## COMMISSIONING

### Train user staff in operation and routine preventative maintenance of equipment.

END OF SECTION