# General

## Related Sections

### Section 01 74 21 – Construction/Demolition, Waste Management and Disposal

### Section 21 13 13 - Wet Pipe Sprinkler Systems.

### Section 21 12 00 – Fire-Suppression Standpipes and Hose Assemblies.

### Section 22 05 00 – Common Work Results for Plumbing.

### Section 23 05 19.13 - Thermometers and Pressure Gauges - Piping Systems

### Section 28 31 00.01 – Mulitplex Fire Alarm System.

### Section 33 11 16.01 – Incoming Site Water Utility Distribution Piping.

## REFERENCES

### American National Standards Institute/National Fire Protection Association (ANSI/NFPA)

#### ANSI/NFPA 13, Standard for the Installation of Sprinkler Systems.

#### ANSI/NFPA 25, Standard for the Inspection, Testing and Maintenance of Water-Based Fire Protection Systems.

### American Society for Testing and Materials (ASTM)

#### ASTM A-234, Standard Specification for Piping Fittings for Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service.

#### ASTM A-536, Standard Specification for Ductile Iron Castings.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

### Underwriter's Laboratories of Canada (ULC)

#### CAN/ULC S543, Internal Lug Quick Connect Coupling for Fire Hose.

## SUBMITTALS

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Shop Drawings:

#### Submit shop drawings and product data in accordance with Section 01 33 00 - Submittal Procedures and in accordance with ANSI/NFPA 13.

##### Shop drawings: submit drawings stamped and signed by designer registered and acceptable to the authority having jurisdiction.

### Samples:

#### Submit samples in accordance with Section 01 33 00 - Submittal Procedures.

#### Submit samples of following:

##### Each type of sprinkler head.

##### Signs and valve tags.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Test reports:

##### Submit certified test reports for packaged fire pumps from approved independent testing laboratories, indicating compliance with specifications for specified performance characteristics and physical properties.

##### Test each pump/driver package at factory to provide detailed performance data and to demonstrate compliance with ANSI/NFPA and specification. Submit certified test curves for approval of Owner.

##### Test hydrostatically to meet requirements of fire protection system to which it will be connected.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

#### Manufacturer's Field Reports: manufacturer's field reports specified.

### Closeout Submittals:

#### Provide maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

#### Provide detailed hydraulic calculations including: summary sheet, Contractor's Material and Test Certificate for aboveground and underground piping, as well as other deliverables for incorporation into manual specified in Section 01 78 00 - Closeout Submittals, in accordance with ANSI/NFPA 13.

## QUALITY ASSURANCE

### Qualifications:

#### Installer: certified journeyperson in dry pipe sprinkler installations with 5 years documented experience approved by manufacturer.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## ENGINEERING DESIGN CRITERIA

### Design system in accordance with ANSI/NFPA 13, using following parameters:

#### Hazard:

##### To suit occupancy.

#### Pipe size and layout:

##### Hydraulic design.

##### Sprinkler head layout: to ANSI/NFPA 13 or as directed by authority having jurisdiction.

#### Water supply:

##### Conduct flow and pressure test of water supply in vicinity of project to obtain criteria for bases of design in accordance with ANSI/NFPA 13.

#### Zoning:

##### System zoning as indicated.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

## MAINTENANCE

### Extra Materials:

#### Provide maintenance materials in accordance with Section 01 78 00 - Closeout Submittals.

#### Provide spare sprinklers and tools as required by ANSI/NFPA 13.

## WARRANTY

### Provide a written guarantee, signed and issued in the name of the owner, against defective materials and workmanship for a period of one (1) year from the date of Substantial Completion.

# PRODUCTS

## PIPE, FITTINGS AND VALVES

### Pipe:

#### Ferrous: to ANSI/NFPA 13.

#### Copper tube: to ANSI/NFPA 13.

### Fittings and joints to ANSI/NFPA 13:

#### Ferrous: screwed, welded, flanged or roll grooved.

#### Copper tube: screwed, soldered, brazed or roll grooved.

#### Fittings:

##### Roll grooved steel pipe:

###### Branch outlets to be accomplished utilizing Mechanical-T branch connectors with locating collar engaging into hole. Provide Grade ‘E’ standard pressure-responsive gasket or o-rings for sealing purposes. Branch outlet connection to be either roll-grooved of female threaded to match branch piping.

###### Sprinkler head connections, branch connections, drop nipples and sprigs shall be made with hole cut outlet-T with female thread outlet connections with locating collar engaging into hole. Provide Grade ‘E’ standard pressure responsive gasket.

###### Pipe fittings such as 90° elbow, 45° elbow, straight tees, etc., shall be of ductile iron to ASTM A-536 or forged steel to ASTM A-234 with grooved or shouldered ends for direct connection into grooved piping systems with steel pipe.

###### Stainless steel braided flexible hose with branch line nipples. Size NPS1/2 and ¾, FM Approved, rated at 1375 kPa, light weight, pre-assembled mounting bracket for T-Bar ceiling.

### Auxiliary valves:

#### ULC listed for fire protection service.

#### Up to NPS 2: bronze, screwed ends, ball valves.

#### NPS 2 1/2 and over: cast iron, flanged or roll grooved ends, indicating butterfly valve or OS & Y gate.

#### Grooved butterfly valves NPS 2 ½ to NPS 10.

##### Ductile iron body to ASTM A-536 coated with a polyphenylene sulphide blend.

##### Disc of ductile iron to ASTM A-536 with EPDM coating providing bubble tight shut off.

##### Grooved ends for installation in grooved steel piping system.

##### Suitable for 2000 kPa working pressure.

##### Provide complete with two single pole, double throw supervisory switches pre-wired monitoring the open position, in weatherproof housing.

##### Manual gear operator.

##### To be utilized in field piping NPS 2 ½ to NPS 10.

#### Swing check valves.

#### Grooved check valves:

##### Ductile iron body to ASTM A-536.

##### Single disc, spring loaded check valve suitable for anti-hammer service.

##### Provide valve drilled, tapped and plugged downstream for drainage outlet.

##### Grade ‘E’ EPDM Deal

##### Grooved ends for installation in grooved steel piping systems.

##### Pressure rated up to 1725 kPa.

#### Ball drip.

#### Valves NPS 1 to NPS 2, threaded or grooved.

##### Ductile iron body to ASTM A-536, painted.

##### Type 316 stainless steel ball.

##### Grooved ends for installation in grooved steel piping systems.

##### Suitable for 2400 kPa working pressure.

##### Provide with double pole, double throw supervisory switch, pre-wired monitoring the open position, in weatherproof housing.

##### Manual gear operator.

#### Tamper devices wired back to fire alarm panel.

### Pipe hangers:

#### ULC listed for fire protection services.

## SPRINKLER HEADS

### General: to ANSI/NFPA 13 and ULC listed for fire services.

## SPRINKLER HEAD TYPE A

### Upright bronze.

## SPRINKLER HEAD TYPE B

### Pendant chrome glass bulb semi-recessed type.

## SPRINKLER HEAD TYPE C

### Pendant chrome glass bulb type.

## SPRINKLER HEAD TYPE D

### Recessed polished chrome glass bulb type with ring and cup.

## SPRINKLER HEAD TYPE E

### Concealed glass bulb type with cover to match ceiling finish.

## SPRINKLER HEAD TYPE F

### Side wall polished chrome glass bulb type.

## AUXILIARY SUPERVISORY SWITCHES

### General: to ANSI/NFPA 13 and ULC listed for fire service.

### Valves:

#### Mechanically attached to valve body, with normally open and normally closed contacts and supervisory capability.

### .Flow switch type:

#### With normally open and normally closed contacts and supervisory capability.

### Pressure alarm switch:

#### With normally open and normally closed contacts and supervisory capability.

## WATER GONG

### To ANSI/NFPA 13 and ULC listed for fire service. Location as indicated.

## FIRE DEPARTMENT CONNECTION

### To ANSI/NFPA 13 and ULC listed, siamese type, location as indicated. Thread specifications to be compatible with local fire department.

### Polished bronze chrome plated exposed with identifying sign cast on plate. Threaded metal caps and chains.

## DRY PIPE VALVE

### ULC listed.

### Cast iron, flanged type, sized to suit water main.

### Components:

#### Accelerator.

#### Air maintenance device with low pressure alarm.

#### Alarm pressure switch with supervisory capability.

#### Pressure gauges.

#### Drain valve.

#### Test valve with associated piping.

#### Shut off valve - OS & Y with tamper-proof device wired back to fire alarm panel.

## PRE-ACTION /DELUGE ALARM VALVE

### ULC listed.

### Cast iron, flanged type, sized to suit water main.

### Components:

#### Accelerator.

#### Air maintenance device with low pressure alarm.

#### Alarm pressure switch with supervisory capability.

#### Test valve and associated piping.

#### Drain valve.

#### Electrical tripping device.

#### Shut off valve - OS & Y with tamper-proof device wired back to fire alarm panel.

## COMPRESSED AIR SUPPLY

### Automatic Air Compressor.

### ULC listed.

### Capacity:

#### To restore normal air pressure in system within 30 minutes, 60 minutes for low differential systems.

#### To provide air pressure of 140 kPa in excess of calculated trip pressure of dry pipe valve in accordance with instruction sheet furnished with dry pipe valve.

### Piping: ferrous, NPS 3/4 screwed joints and fittings, to ANSI/NFPA 13.

## PRESSURE GAUGES

### ULC listed and to Section 23 05 19.13 - Thermometers and Pressure Gauges - Piping Systems.

### Maximum limit of not less than twice normal working pressure at point where installed.

## RELIEF VALVE

### ULC listed.

## SPARE PARTS CABINET

### For storage of maintenance materials, spare sprinkler heads and special tools.

### Construct to sprinkler head manufacturers standard.

# EXECUTION

## MANUFACTURER'S INSTRUCTIONS

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## INSTALLATION

### Install, inspect and test to acceptance in accordance with ANSI/NFPA 13 and NFPA 25.

### Testing to be witnessed by authority having jurisdiction.

### Install water gong as indicated.

### Install fire department connections as indicated.

### Install spare parts cabinet as indicated.

### Pressure gauges:

#### Location:

##### On water side and air side of dry pipe valve.

##### At air receiver.

##### In each independent pipe from air supply to dry pipe valve.

##### At exhausters and accelerators.

#### Install to permit removal.

#### Locate so as not subjected to freezing.

### Valve identification:

#### Identify drain valve, by-pass valves and main shut-off valve and all auxiliary valves.

## FIELD QUALITY CONTROL

### Manufacturer's Field Services:

#### Obtain written report from manufacturer verifying compliance of Work, in handling, installing, applying, protecting and cleaning of product and submit Manufacturer's Field Reports as described in PART 1 - SUBMITTALS.

#### Provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions.

#### Schedule site visits, to review Work, as directed in PART 1 - QUALITY ASSURANCE.

## CLEANING

### Proceed in accordance with Section 01 74 00 - Cleaning

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION