# GENERAL

## Summary

### Section Includes:

#### Thermal insulation for piping and piping accessories in commercial type applications.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 07 92 00 – Joint Sealing.

### Section 22 07 16 – Plumbing Equipment Insulation.

### Section 23 05 53.01 – Mechanical Identification.

## References

### American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE)

#### ASHRAE Standard 90.1, Energy Efficient Design of New Buildings Except Low-Rise Residential Buildings (Including all Addenda).

### American Society for Testing and Materials (ASTM)

#### ASTM B209M, Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate Metric.

#### ASTM C335, Standard Test Method for Steady State Heat Transfer Properties of Horizontal Pipe Insulation.

#### ASTM C411, Standard Test Method for Hot-Surface Performance of High-Temperature Thermal Insulation.

#### ASTM C449/C449M, Standard Specification for Mineral Fibre-Hydraulic-Setting Thermal Insulating and Finishing Cement.

#### ASTM C533 Standard specification for Calium Silicate Insulation Block and Pipe.

#### ASTM C547 Standard Specification for Mineral Fibre Pipe Insulation.

#### ASTM C795, Standard Specification for Thermal Insulation for Use in Contact with Austenitic Stainless Steel.

#### ASTM C921, Standard Practice for Determining the Properties of Jacketing Materials for Thermal Insulation.

#### ASTM D1784, Standard Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds.

### Canadian General Standards Board (CGSB)

#### CGSB 51-GP-52Ma, Vapour Barrier, Jacket and Facing Material for Pipe, Duct and Equipment Thermal Insulation.

#### CAN/CGSB-51.53, Poly (Vinyl Chloride) Jacketting Sheet, for Insulated Pipes, Vessels and Round Ducts

### Department of Justice Canada (Jus)

#### Canadian Environmental Assessment Act (CEAA), c. 37.

#### Canadian Environmental Protection Act, (CEPA), c. 33.

#### Transportation of Dangerous Goods Act (TDGA), c. 34.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Material Safety Data Sheets.

### Manufacturer's Trade Associations

#### Thermal Insulation Association of Canada (TIAC): National Insulation Standards.

### Underwriters' Laboratories of Canada (ULC)

#### CAN/ULC-S102, Surface Burning Characteristics of Building Materials and Assemblies.

### National Energy Code for Buildings (NECB).

## Definitions

### For purposes of this section:

#### "CONCEALED" - insulated mechanical services in suspended ceilings and non-accessible chases and furred-in spaces.

#### "EXPOSED" - will mean "not concealed" as defined herein.

### TIAC ss:

#### CRF:  Commercial Rectangular Finish

#### CPF: Commercial Piping Finish.

## SUBMITTALS

### Submittals:  in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Samples:

#### Submit samples in accordance with Section 01 33 00 - Submittal Procedures.

#### Submit for approval: complete assembly of each type of insulation system, insulation, coating, and adhesive proposed. Mount sample on 12 mm plywood board. Affix label beneath sample indicating service.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions to Owner.

## QUALITY ASSURANCE

### Qualifications:

#### Installer: certified in performing work of this Section, and have at least 5 years successful experience in this size and type of project, qualified to standards of TIAC.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## delivery, storage and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

#### Deliver materials to site in original factory packaging, labeled with manufacturer's name, address.

### Storage and Protection:

#### Protect from weather, construction traffic.

#### Protect against damage.

#### Store at temperatures and conditions required by manufacturer.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Place excess or unused insulation and insulation accessory materials in designated containers.

#### Divert unused metal materials from landfill to metal recycling facility approved by Owner.

#### Dispose of unused adhesive material at official hazardous material collections site approved by Owner.

# Products

## Fire and Smoke Rating

### In accordance with CAN/ULC-S102.

#### Maximum flame spread rating: 25.

#### Maximum smoke developed rating: 50.

## Insulation

### Mineral fibre specified includes glass fibre, rock wool, slag wool.

### Thermal conductivity ("k" factor) not to exceed specified values at 24o C mean temperature when tested in accordance with ASTM C335.

### TIAC Code A-2: Rigid moulded calcium silicate in sections and blocks, and with special shapes to suit project requirements.

#### Insulation: to ASTM C533.

#### Maximum "k" factor: to 0.075 W/m o C @ 500o C.

#### Design to permit periodic removal and re-installation.

### TIAC Code A-3: Rigid moulded mineral fibre with factory applied vapour retarder jacket.

#### Mineral fibre: to CAN/ULC-S702 and ASTM C547.

#### Jacket: to CGSB 51-GP-52Ma.

#### Maximum "k" factor: to CAN/ULC-S702.

### TIAC Code A-6: Flexible unicellular tubular elastomer.

#### Insulation: with vapour retarder jacket to ASTM C534.

#### Jacket: to CGSB 51-GP-52Ma.

#### Maximum "k" factor: 0.039 W/m – oC.

#### To be certified by manufacturer to be free of potential stress corrosion cracking corrodants.

#### Flame spread index less than 25, and smoke developed index less than 50.

### TIAC Code C-2: Mineral fibre blanket faced with factory applied vapour retarder jacket (as scheduled in PART 3 of this section).

#### Mineral fibre: to CAN/ULC-S702.

#### Jacket: to CGSB 51-GP-52Ma.

#### Maximum "k" factor: to CAN/ULC-S702.

## Insulation Securement

### Tape: Self-adhesive, aluminum, plain reinforced, 50 mm wide minimum.

### Contact adhesive: Quick setting.

### Canvas adhesive: Washable.

### Tie wire: 1.5 mm diameter stainless steel.

### Bands: Stainless steel, 19 mm wide, 0.5 mm thick.

## Cement

### Thermal insulating and finishing cement:

#### Hydraulic setting or air drying on mineral wool, to ASTM C449/C449M.

## Vapour Retarder Lap Adhesive

### Water based, fire retardant type, compatible with insulation.

## Indoor Vapour Retarder Finish

### Vinyl emulsion type acrylic, compatible with insulation.

## Outdoor Vapour Retarder Finish

### Vinyl emulsion type acrylic, compatible with insulation.

### Reinforcing fabric: Fibrous glass, untreated 305 g/m2.

## Jackets

### Polyvinyl Chloride (PVC):

#### One-piece moulded type and sheet to CAN/CGSB-51.53 with pre-formed shapes as required.

#### Colours: to match adjacent finish paint.  Confirm colour with Owner.

#### Minimum service temperatures: -20o C.

#### Maximum service temperature: 65o C.

#### Moisture vapour transmission: 0.02 perm.

#### Thickness: 0.55 mm.

#### Fastenings:

##### Use solvent weld adhesive compatible with insulation to seal laps and joints.

##### Tacks.

##### Pressure sensitive vinyl tape of matching colour.

#### Special requirements:

##### Indoor: flame spread rating 25, smoke developed rating 50.

##### Outdoor: UV rated material at least 0.5 mm thick.

### Canvas:

#### 220gm/m2 cotton, plain weave, treated with dilute fire retardant lagging adhesive to ASTM C921.

#### Lagging adhesive: Compatible with insulation.

### Aluminum:

#### To ASTM B209.

#### Thickness: 0.50 mm sheet.

#### Finish:  Embossed or corrugated.

#### Joining: Longitudinal and circumferential slip joints with 50 mm laps.

#### Fittings: 0.5 mm thick die-shaped fitting covers with factory-attached protective liner.

#### Metal jacket banding and mechanical seals: stainless steel, 19 mm wide, 0.5 mm thick at 300 mm spacing.

### Stainless steel:

#### Type: 304 or type 316.

#### Thickness: 0.25 mm.

#### Finish: Smooth.

#### Joining: Longitudinal and circumferential slip joints with 50 mm laps.

#### Fittings: 0.5 mm thick die-shaped fitting covers with factory-attached protective liner.

#### Metal jacket banding and mechanical seals: stainless steel, 19 mm wide, 0.5 mm thick at 300 mm spacing.

## Weatherproof Caulking FOR JACKETS Installed Outdoors

### Caulking to: Section 07 92 00 - Joint Sealing.

# Execution

## MANUFACTURE’S instructions

### Compliance:  comply with manufacturer’s written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Pre- Installation Requirement

### Pressure testing of piping systems and adjacent equipment to be complete, witnessed and certified.

### Surfaces to be clean, dry, free from foreign material.

## Installation

### Install in accordance with TIAC National Standards.

### Apply materials in accordance with manufacturer’s instructions and this specification.

### Use two layers with staggered joints when required nominal wall thickness exceeds 75 mm.

### Maintain uninterrupted continuity and integrity of vapour retarder jacket and finishes.

#### Install hangers, supports outside vapour retarder jacket.

### Supports, Hangers:

#### Apply high compressive strength insulation, suitable for service, at oversized saddles and shoes where insulation saddles have not been provided.

## Removable, Pre-fabricated, Insulation and Enclosures

### See Section 22 07 16 – Plumbing Equipment Insulation.

## Installation of Elastomeric Insulation

### Insulation to remain dry. Overlaps to manufacturers instructions. Ensure tight joints.

### Provide vapour retarder as recommended by manufacturer.

## Piping Insulation Schedules

### Includes valves, valve bonnets, strainers, flanges and fittings unless otherwise specified. Insulate vent pipes 3.0 m from roof penetration.

### TIAC Code: A-2.

#### Insulation securements: 18 ga SS wire or 12 mm x 0.51 mm SS bands at 300 mm oc.

#### Seals: lap seal adhesive, lagging adhesive.

#### Installation: TIAC Code: 1501-H.

### TIAC Code: A-3.

#### Securements: Tape at 300 mm oc.

#### Seals: VR lap seal adhesive, VR lagging adhesive.

#### Installation: TIAC Code: 1501-C.

### TIAC Code: A-6.

#### Insulation securements: as per manufacturer’s recommendation.

#### Seals: lap seal adhesive, lagging adhesive.

#### Installation: TIAC Code: 1501-CA.

### TIAC Code: C-2 with vapour retarder jacket.

#### Insulation securements: 18 ga SS wire or 12 mm x 0.5 mm SS bands at 300 mm oc.

#### Seals: lap seal adhesive, lagging adhesive.

#### Installation: TIAC Code: 1501-C.

### Thickness of insulation to be as listed in following table.

#### Run-outs to individual units and equipment not exceeding 4000 mm long.

#### Do not insulate exposed runouts to plumbing fixtures, chrome plated piping, valves, fittings.

| Application | Temp oC | TIAC code | Pipe sizes (NPS) and insulation thickness (mm) |
| --- | --- | --- | --- |
|  | Run out |  |  | to 1 | 1 1/4 to 2 | 2 1/2 to 4 | 5 to 6 | 8 & over |
| Steam | up to 175 | A-3 | 38 | 50 | 65 | 75 | 90 | 90 |
| Domestic HWS |  | A-3 | 25 | 25 | 25 | 38 | 38 | 38 |
| Refrigerated Drinking Water |  | A-3 | 25 | 25 | 25 | 25 | 25 | 25 |
| Domestic CWS |  | A-3 | 25 | 25 | 25 | 25 | 25 | 25 |
| RWL and RWP |  | A-3 | 25 | 25 | 25 | 25 | 25 | 25 |
| Roof Drain Body |  | C-2 | 25 | 25 | 25 | 25 | 25 | 25 |
| Vent Pipe Plumbing |  | A-3 | 25 | 25 | 25 | 25 | 25 | 25 |

### Finishes:

#### Exposed indoors: PVC jacket.

#### Exposed in mechanical rooms:  PVC jacket.

#### Concealed, indoors: canvas on valves, fittings. No further finish.

#### Use vapour retarder jacket on TIAC code A-3 insulation compatible with insulation.

#### Outdoors: Water-proof Aluminium, or SS jacket.

#### Finish attachments: SS screws or bands, at 150 mm oc. Seals: wing or closed.

#### Installation: To appropriate TIAC code CPF/1 through CPF/5.

## CLeaning

### Proceed in accordance with Section 01 74 00 – Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION