# General

## summary

### Section includes:

#### Materials and installation for plumbing pumps.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

## References

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS)

## submittals

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Submit manufacturer’s printed product literature, specifications and data sheet for fixtures and equipment.

#### Submit WHMIS SDS in accordance with Section 01 33 00 - Submittal Procedures.  Indicate VOC’s for adhesive and solvents during application and curing.

### Shop Drawings:

#### Submit shop drawings to indicate:

##### Equipment, including connections, fittings, control assemblies and ancillaries.  Identify whether factory or field assembled.

##### Wiring and schematic diagrams.

##### Dimensions and recommended installation.

##### Pump performance and efficiency curves.

### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions: submit manufacturer’s installation instructions.

### Manufacturers’ Field Reports: manufacturers’ field reports specified.

### Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 – Closeout submittals, include:

#### Manufacturers name, type, model year, capacity and serial number.

#### Details of operation, servicing and maintenance.

#### Recommended spare parts list with names and addresses.

## QUALITY ASSURANCE

### Pre-Installation Meeting:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installation.

##### Verify project requirements.

##### Review installation and substrate conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer’s installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction /Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

#### Unused sealant materials must not be disposed of into sewer system, into streams, lakes, onto ground or in other location where it will pose health or environmental hazard.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

# Products

## Domestic Hot Water Circulating Pumps

### Capacity: see pump schedule.

### Construction: closed-coupled, in-line centrifugal, all bronze or stainless steel, construction, stainless steel shaft, stainless steel or bronze shaft sleeve, two oil lubricated bronze sleeves or ball bearings. Design for 860 kPa wp and 105° C continuous service.

### Motor: drip proof, with thermal overload protection.

### Supports: provide as recommended by manufacturer.

## Domestic Water Booster System

### Packaged duplex or triplex system as indicated, factory assembled, tested and adjusted, ready for site piping and electrical connections, diaphragm tank.

### Total capacity:

#### Flow rate: see pump schedule.

#### System pressure: see pump schedule.

#### Available pressure at meter outlet: see pump schedule.

#### Duplex system with 25% on lead pump and 75% on lag pump.

#### Triplex system with 20% on lead pump and 40% on each lag pump.

### Construction: vertical, in-line split coupled centrifugal, or multi stage split coupled centrifugal, cast-iron casing, bronze or stainless impeller, stainless steel shaft sleeve, mechanical shaft seal, designed for 860 kPa suction pressure. Include hydropneumatic pressure tank to prevent starts at low flows.

### Valves: to Section 22 11 18 - Domestic Water Piping Copper. Suction and discharge ball or butterfly valves and pressure reducing and check valve for each pump pressure sustaining valve required if variable frequency drive used, silent check valve on each pump connected to common Sch. 10 stainless steel suction and discharge headers.

### Motors:  premium efficiency and for variable frequency drive.

### Supports: install complete package on factory fabricated stainless steel structural steelwork.

### Anchor bolts and templates:

#### Supply for installation by other Divisions.

### Control panel: CSA 4 enclosure complete with:

#### Externally operated disconnect switch.

#### Magnetic across-the-line fused starters and variable frequency drive (VFD) with bypass contactor for lead pump: VFD mounted in control cabinet and rotates among all pumps

#### Overload protection for each phase.

#### Adjustable pressure transmitter.

#### Low pressure safety cut-out.

#### Control circuit transformer with fused secondary.

#### Adjustable time delay relay.

#### Hand-off-automatic selector switch for pumps.

#### Pressure and suction gauges, to Section 23 05 19.13 – Thermometers and Pressure Gauges – Piping Systems, two times operating pressure.

#### Pilot lights; power on, low suction pressure, pump run, system fault.

#### Lead/lag selector switch.

#### Alarm: visual and audible with silencing switch for abnormal conditions.

#### Microprocessor with LCD display.

#### Phase failure protection.

#### Lightning protection.

#### Ammeter, voltmeter, audible system fault alarm.

#### Fault alarm contacts to building EMCS.

#### Pump elapsed time meters.

#### Emergency/normal switches (bypass VFD).

### Operation:

#### Automatic cascade control of pumps.

#### Automatic changeover between pumps in operation (ensures the same number of operating hours for all pumps).

#### Stop function when operating at low flow (increases the efficiency when operating at low flow).

#### Manual operation (enables testing of individual pumps).

#### Various setpoint influences:

##### Friction-loss compensation (decreasing pressure with decreasing flow)

##### Setpoint adjustment via external signals (temperature, time, level and flow).

#### Various digital remote-control functions:

##### Start/stop of system

##### Reduced operation (limits the max. number of pumps in operation)

##### 2-point control of the setpoint (enables control of the setpoint by means of 2-point contact)

##### 3-point control of the setpoint (enables control of the setpoint by means of 3-point contact)

##### Emergency flow operation (aids in firefighting)

#### Pump and system monitoring functions:

##### High and low system pressure shutdown

##### Inlet pressure measurement

##### Motor protection

##### BUS communication

#### Display, alarm and signal functions:

##### LCD display

##### Signal lights for operating and fault indication (green and red light-emitting diodes)

##### Potential-free changeover contacts for operating and fault signals.

#### Clock program

##### Up to 10 different setpoints per 24 hour period

## Sump Pump Vertical Shaft

### Capacity: as per pump schedule.

### Construction: simplex or duplex as indicated.

#### Vertical shaft centrifugal, cast iron case, bronze impeller, stainless steel shaft.

#### Column and cast iron parts protected with baked epoxy paint.

#### Cast iron inlet strainer cover plate and curb frame.

#### Vertical outlet case tapped for NPS 1-½.

#### Grease lubricated ball bearing and intermediate bronze sleeve column type bearings with grease fitting.

### Motor: rated for continuous duty, built-in overload protection, drip-proof, complete with three m of three-wire rubber covered cord.

### Control: ball and rod mechanical float switch and mechanical alternator for duplex pumps.  Compression type high water alarm.

### Control Panel

- CSA approved

- Main disconnect

- Thermal and short circuit protection using circuit breakers.

- Failure protection with automatic switch over to non-operating pump for duplux units.

- Control transformer with fused primary.

- Power on and pump run pilot lights.

- Hand-off-auto selector switch.

- Nema 4 enclosure.

- High level alarm with reset button.

- Overload pilot lights.

- Elapsed time meter.

- Magnetic starter.

## Sump Pump Submersible

### Capacity: see pump schedule.

### Construction: simplex  CSA approved, housing epoxy coated cast iron or stainless steel, stainless steel shaft, non-clog bronze impeller, mechanical shaft seal, strainer or as indicated in pump schedule.

### Motor: hermetically sealed, with automatic overload protection.

### Control: integral diaphragm type level control buoyant case and switch, plug and cord.

## Bilge and Sewage Pump

### Capacity: as per pump schedule.

### Construction:  duplex, submersible centrifugal, designed to handle 50 mm solids and for sump depth as indicated, all iron construction, semi-open dynamically balanced bronze or cast iron impeller, automatic lubricated bronze bearings.

### Motor: drip-proof, with overload and under voltage protection.

### Control: copper ball float operated heavy duty switch. Starter switch on cover plate. Automatic electric alternator with selector relays to alternate or activate both pumps. Adjustable float stops on stainless steel brass rod.

### Alarm: low voltage powered audible and visual alarm controlled by float operated switch.

### Control Panel.

- CSA approved

- Main disconnect

- Power on and pump run pilot lights.

- Elapsed time meter

- Lightning arrestor.

- Control transformer with circuit breakers

- High level alarm with contacts to building’s EMCS system.

- Motors starter with overload protection and overload indication.

- Pump alternator.

### Sump:  fibreglass reinforced plastic or concrete, as indicated, one piece, to manufacturer’s standard, with heavy bituminous coating inside and out, or concrete as indicated in Section 03 30 00 – Cast-in-Place Concrete.

# Execution

## MANUFACTURER’S INSTRUCTIONS

### Compliance: comply with manufacturer’s written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and data sheet.

## Installation

### Make piping and electrical connections to pump and motor assembly and controls as indicated.

### Ensure pump and motor assembly do not support piping.

### Align vertical pit mounted pump assembly after mounting and securing cover plate.

### Place 150 mm sand under sump pit tank.

## Field Quality Control

### Check power supply.

### Check starter protective devices.

### Start-up, check for proper and safe operation.

### Check settings and operation of hand-off-auto selector switch, operating, safety and limit controls, audible and visual alarms, over-temperature and other protective devices.

### Adjust flow from water-cooled bearings.

### Adjust impeller shaft stuffing boxes, packing glands.

## Start-up

### General:

#### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements, supplemented as specified herein.

#### Procedures:

##### Check power supply.

##### Check starter O/L heater sizes.

##### Start pumps, check impeller rotation.

##### Check for safe and proper operation.

##### Check settings, operation of operating, limit, safety controls, over-temperature, audible/visual alarms, other protective devices.

##### Test operation of HOA switch.

##### Test operation of alternator.

##### Adjust leakage through water-cooled bearings.

##### Adjust shaft stuffing boxes.

##### Adjust leakage flow rate from pump shaft stuffing boxes to manufacturer's recommendations.

##### Check base for free-floating, no obstructions under base.

##### Run-in pumps for 12 continuous hours.

##### Check installation, operation of mechanical seals, packing gland type seals. Adjust as necessary.

##### Adjust alignment of piping and conduit to ensure full flexibility at all times.

##### Eliminate causes of cavitations, flashing, air entrainment.

##### Measure pressure drop across strainer when clean and with flow rates as finally set.

##### Replace seals if pump used to degrease system or if pump used for temporary heat.

##### Verify lubricating oil levels.

## Domestic HW Circulating Pumps

### Balance flows using circuit setter balancing valve.

## Performance Verification (PV) Pressure Booster Pumps

### General:

#### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements: supplemented as specified herein.

### Obtain manufacturer's approval, before performing PV, to ensure warranties remain intact.

### Application tolerances:

#### Flow: +/- 10%.

#### Pressure: Plus 20%, minus 5%.

### PV procedures:

#### Open pump balancing valve fully.

#### Measure differential pressure (DP) across pump.

#### Measure amperage and voltage and compare with manufacturer's data sheets and motor nameplate data.

#### If suction is different size than discharge connection, add velocity head correction factor to DP.

#### Mark this DP on manufacturer's pump curve.

#### If flow rate is higher than specified, slow close balancing valve until specified DP is reached.

#### Repeat measurements of amps and volts. Compare with manufacturer's data sheets.

#### Calculate BHP and compare with nameplate data.

## Performance Verification (PV) - Tankless Pressure Booster System

### Pumps: As specified above.

### PV of complete unit:

#### Test performance of pumps in lead and in lag position.

#### Test operation of alternator.

#### Simulate failure of pumps in possible combinations such as:

##### Failure of each "lead" pump.

##### Failure of first "lag" pump, then 2nd "lag" pump, etc.

#### Test operation by simulating 0%, 10%, 25%, 50%, 75%, 100% and 110% of design load and for one hour. Record pressure at:

##### Which lead and lag pump cut in and cut out.

##### Water meter outlet.

##### "Worst" plumbing fixture.

#### Verify operation and control of over-temperature protection devices.

## Performance Verification (PV) - Hydropneumatic Pressure Booster System

### Pumps: As specified above.

### PV of complete unit:

#### Test performance of pumps in lead and in lag position.

#### Test operation of alternator.

#### Simulate failure of pumps in possible combinations such as:

##### Failure of each "lead" pump.

##### Failure of first "lag" pump, then 2nd "lag" pump, etc.

#### Test operation by simulating 0%, 10%, 25%, 50%, 75%, 100% and 110% of design load and for one hour. Record pressure at:

##### Which lead and lag pump cut in and cut out.

##### Water meter outlet.

##### "Worst" plumbing fixture.

#### Verify operation and control of over-temperature protection devices.

## PV - Sanitary and Storm Water Pumps

### Application tolerances:

#### Flow: Plus 10%; Minus 0%.

#### Pressure: Plus 10%; Minus 5%.

### PV Procedures:

#### Fill sump at rate slower than capacity of pump #1.

#### Record levels at which pump #1 starts and stops. Determine flow rate by observing time taken to draw down water level.

#### Fill sump at rate faster than capacity of pump #1 but slower than capacities of pumps #1 and #2 operating in parallel.

#### Record levels at which pumps start and stop - water level rising and water level falling.

#### Verify operation of alternator.

#### Adjust water level controls as necessary.

#### Fill sump at rate faster than capacities of pumps #1 and #2 operating in parallel.

#### Record levels at pump starts and stops - water level rising and falling.

#### Check operation of alternator.

#### Adjust level controls as necessary.

#### Check level at which high water level alarm starts and stops. Adjust as necessary.

### Check removeability of pumps for servicing without interfering with installation or operation of other equipment.

### Verify non-clog capability and maximum size of solids, using procedures recommended by manufacturer.

## Reports

### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements: supplemented as specified herein.

### Include

#### PV results on approved PV Report Forms.

#### Product Information report forms.

#### Pump performance curves (family of curves) with final point of actual performance marked thereon.

## Training

### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements supplemented as specified herein.

END OF SECTION