# General

## summary

### Section includes:

#### The installation of drainage waste and vent piping – cast iron and copper.

## Related Sections

### Section 01 35 29.06 - Health and Safety Requirements.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 22 05 00 – Common Work Results for Plumbing.

## References

### American Iron and Steel Institute (AISI)

#### AISI 304, Stainless Steel.

### American Society for Testing and Materials (ASTM)

#### ASTM B32, Specification for Solder Metal.

#### ASTM B306, Specification for Copper Drainage Tube (DWV).

#### ASTM C564, Specification for Rubber Gaskets for Cast Iron Soil Pipe and Fittings.

### Canadian Standards Association (CSA International)

#### CAN/CSA-B70, Cast Iron Soil Pipe, Fittings and Means of Joining.

#### CAN/CSA- B125.3, Plumbing Fittings.

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

## Submittals:

### Provide submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Provide manufacturer's printed product literature and datasheets for adhesives, and include product characteristics, performance criteria, physical size, finish and limitations.

# Products

## Copper Tube and Fittings

### Above ground sanitary, storm and vent Type DWV to: ASTM B306.

#### Fittings.

##### Cast brass: to CAN/CSA-B125.

##### Wrought copper: to CAN/CSA-B125.

#### Solder: tin-lead, 50:50, type 50A or tin-antimomy only 95:5, type TA to ASTM B32.

## Cast Iron Piping and Fittings

### Buried sanitary, storm and vent minimum NPS2, to: CAN/CSA-B70, with one layer of protective coating of butimous.

#### Joints.

##### Mechanical joints.

###### Neoprene or butyl rubber compression gaskets: to ASTM C564 or CAN/CSA-B70.

###### Stainless steel clamps.

##### Hub and spigot.

###### Neoprene gasket: to CSA B70.

###### Cold caulking compounds.

### Above ground sanitary, storm and vent: to CAN/CSA-B70.

#### Joints.

##### Mechanical joints.

###### Neoprene or butyl rubber compression gaskets with stainless steel clamps.

## Stainless Steel Pipe and Fittings

### Above ground and buried sanitary, storm and vent, NPS 2 to NPS 10, stainless steel, type AISI 304.

#### Mechanical Joints:

##### Push-fit socket joint with EPDM sealing ring.

# Execution

## Installation

### In accordance with Section 23 05 05 – Installation of Pipework and by certified journeyperson.

### Install in accordance with Canadian Plumbing Code and local authority having jurisdiction.

## Testing

### Pressure test buried systems before backfilling.

### Hydraulically test to verify grades and freedom from obstructions.

## Performance Verification

### Cleanouts:

#### Ensure accessible and that access doors are correctly located.

#### Open, cover with linseed oil and re-seal.

#### Verify that cleanout rods can probe as far as the next cleanout, at least.

### Test to ensure traps are fully and permanently primed.

### Storm water drainage:

#### Verify domes are secure.

#### Ensure weirs are correctly sized and installed correctly.

#### Verify provisions for movement of roof system.

### Ensure that fixtures are properly anchored, connected to system and effectively vented.

### Affix applicable label (storm, sanitary, vent, pump discharge, etc.) c/w directional arrows every floor or 4.5 m (whichever is less).

### Provide copies of test reports for Commissioning Manuals.

END OF SECTION