# General

## summary

### Section includes:

#### The installation of drainage waste and vent piping – plastic.

## Related Sections

### Section 01 35 29.06 - Health and Safety Requirements.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 22 05 00 – Common Work Results for Plumbing.

## References

### American Society for Testing and Materials (ASTM)

#### ASTM D2235, Specification for Solvent Cement for Acrylonitrille-Butadiene-Styrene (ABS) Plastic Pipe and Fittings.

#### ASTM D2564, Specification for Solvent Cements for Poly(Vinyl-Chloride) (PVC) Plastic Piping Systems.

### Canadian Standards Association (CSA)

#### CSA-B1800 Series, ABS Drain, Waste and Vent Pipe and Pipe Fittings.

#### CSA-B181.2, PVC Drain, Waste and Vent Pipe and Pipe Fittings.

#### CSA-B182.1, Plastic Drain and Sewer Pipe and Pipe Fittings.

### Underwriters Laboratory of Canada (ULC)

#### CAN/ULC-S102.2 Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

## Submittals:

### Provide submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Provide manufacturer's printed product literature and datasheets for piping and adhesives, and include product characteristics, performance criteria, physical size, finish and limitations.

# Products

## Piping and Fittings

### For buried DWV piping to:

#### CSA-B181.1.

#### CSA-B181.2.

#### CSA-B182.1.

### For aboveground DWV piping for combustible construction to:

#### CSA – B181.2

### For aboveground DWV piping for non-combustible construction:

#### Flame spread rating less than 25 and smoke developed classification less than 50.

#### CSA B181.2

## Joints

### Solvent weld for PVC: to ASTM D2564.

#### NPS 1 ½ to 6: one step or two step cement

#### NPS 8 and above: two step cement.

### Solvent weld for ABS: to ASTM D2235.

# Execution

## Installation

### In accordance with Section 23 05 05 - Installation of Pipework and certified journeyperson.

### Install in accordance with Canadian Plumbing Code and local authority having jurisdiction.

## Testing

### Pressure test buried systems before backfilling in accordance with Canadian Plumbing Code.

### Hydraulically test to verify grades and freedom from obstructions.

## Performance Verification

### Cleanouts:

#### Ensure accessible and that access doors are correctly located.

#### Open, cover with linseed oil and re-seal.

#### Verify cleanout rods can probe as far as the next cleanout, at least.

### Test to ensure traps are fully and permanently primed.

### Storm water drainage:

#### Verify domes are secure.

#### Ensure weirs are correctly sized and installed correctly.

#### Verify provisions for movement of roof system.

### Ensure fixtures are properly anchored, connected to system and effectively vented.

### Affix applicable label (storm, sanitary, vent, pump discharge etc.) c/w directional arrows in accordance with Section 23 05 53.01 – Mechanical Identification.

### Provide copies of test reports for Commissioning Manuals.

END OF SECTION