# General

## summary

### Section includes:

#### The installation of drainage waste and vent piping – corrosion resistant.

## RELATED SECTIONS

### Section 01 33 00 – Submittals Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 22 05 00 – Common Work Results for Plumbing.

## References

### American Iron and Steel Institute (AISI)

#### AISI 316L Stainless Steel.

### American Society for Testing and Materials (ASTM)

#### ASTM B117, Standard Practice for Operating Salt Spray (FOG) Apparatus.

#### ASTM D635, Standard Test Method for Rate of Burning and/or Extent and Time of Burning of Plastics in a Horizontal Position.

#### ASTM D2843, Standard Test Method for Density of Smoke from the Burning or Decompositions of Plastics.

#### ASTM3222, Standard Specification for Unmodified Poly (Vinylidene Fluoride) (PVDF) Molding Extrusion and Coating Materials.

#### ASTM D4101, Standard Specification for Polypropylene Injection and Extrusion Materials.

#### ASTM E-84, Standard Test for Surface Burning Characteristics of Building Materials.

#### ASTM F1412, Standard Specification for Polyolefin Pipe and Fittings for Corrosive Waste Drainage Systems.

#### ASTM F1673, Standard Specification for Polyvinylidene Fluoride (PVDF) Corrosion Waste Drainage System.

### Canadian Standards Association (CSA)

#### CSA-B181.3, Polyolefin and Polyvinylidene fluoride (PVDF) Laboratory Drainage System.

### Underwriters Laboratories (UL):

#### UL 94, Test for Flammability of Plastic Materials for Parts in Devices and Appliances.

#### UL 723, Test for Surface Burning Characteristics of Building Materials.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

# Products

## Corrosion Resistant

### General:

#### All corrosion resistant piping, as indicated on drawings, shall discharge into a non-corrosive, acid-resistant waste system.  All drainage and vent piping in this system to be constructed of corrosion-resistant materials described herein.

#### All drains of this system to be collected and discharged into chemical neutralization tank for neutralization before discharging into the building sanitary sewer.  See specification Section 22 05 15 – Plumbing Specialties and Accessories, for details of dilution tanks.

### Above floor piping except in horizontal service spaces or vertical shafts i.e. plenums):

#### All drainage pipe run above ground including traps, waste and branch vents to be Schedule 40 polyolefin materials as detailed in N.B.C. 2.2.8.1. (1) (c) for corrosive waste drainage systems as well as PVDF to CSA B-181.3 and Borosilicate glass to ASTM C1053.  The system to include all straight lengths, fittings and traps, couplings and hanger supports as well as adapters to connect to the tail pieces of sinks.

#### All piping to be installed free of strain.  Horizontal runs to be supported by hangers spaced at 1.2 m centres.  Vertical risers to be supported at floor by riser clamps to prevent lateral and downward movement.

#### All corrosion resistant drainage piping to be joined using the manufacturers recommended method for their system. Joints to be fabricated from material similar to that utilized in pipe. All drainage materials used in the corrosive waste system shall conform to N.B.C. 2.2.8.1. (1) and be suitable for the purpose as per N.P.C. 2.2.1.1. (2)

#### All flame retardant polypropylene piping wall and floor penetrations through fire separations to be provided with ULC (Underwriters Listed for Canada) rated fire stop assemblies to provide a minimum 1 hour fire stop.

#### Fill openings between wall and/or floor and piping at penetrations through fire separations, with annular space greater than 6 mm with high density rock wool insulation.  Provide sufficient void space to seal with fire stop sealant.

#### Provide fire stop sealant between wall and/or floor and pipe at penetrations through fire separations with annular space less than 6 mm.

#### Provide fire stop collars at either side of fire separation wall penetrations and one side only for fire separation floor penetrations.  Secure collars in place with fastening hooks secured with either toggle bolts (gyproc) or anchors (concrete).

#### Supply and install 18 gauge metal pan enclosure around pipe openings in concrete floors on metal deck.

### Above floor piping in horizontal service spaces (i.e. plenums) except for within vertical shaft spaces:

#### All drainage pipe run above ground in horizontal service spaces including traps, waste and branch vents to be Schedule 40, PVDF polyvinylidene fluoride or borosilicate glass to ASTM C1053.  The system to include all straight lengths, fittings and traps, couplings and hanger supports.

#### All piping to be installed free of strain.  Horizontal pipes to be supported by hangers spaced at 1.2 m centres.  Vertical risers to be supported at floor by riser clamps to prevent lateral and downward movement.

#### All corrosion resistant drainage piping to be joined utilizing compression joints. Joints to be fabricated from material similar to that utilized in pipe.

#### All PVDF corrosion resistant pipe shall meet 25 flame spread, 50 smoke developed and be certified to CAN ULC S102.2 Standard UL.

#### All PVDF piping wall and floor penetrations to be provided with ULC (Underwriters Laboratories for Canada) rated fire stop assemblies to provide a minimum 1 hour fire stop.

#### Fill openings between wall and/or floor and piping at penetrations through fire separations with annual space greater than 6 mm with high density rock wool insulation.  Provide sufficient void space to seal with fire stop sealant.

#### Provide fire stop sealant between wall and/or floor and pipe at penetrations through fire separations with annular space less than 6 mm.

#### Provide fire stop collars at either side of fire separation wall penetrations and one side only for fire separation floor penetrations.  Secure collars in place with fastening hooks secured with either toggle bolts (gyproc) or anchors (concrete).

#### Supply and install 18 gauge metal pan enclosure around pipe openings in concrete floors on metal deck.

### Below ground piping:

#### All drainage pipe run below ground including traps, waste and vent piping to be Schedule 40 polyolefin materials as described in N.B.C. 2.2.8.1. for corrosive waste drainage. The system to include all straight lengths, fittings and traps, couplings.  Corrosive waste piping shall be joined using fusion type fittings as per the manufacturers approved methodology and equipment for their system.

#### All underground piping to be jointed using fusion jointing methodology. Compression joints and /or mechanical joints shall not be acceptable below ground.

#### All underground piping to be installed on a bed of cleaned washed sand 150 mm deep. Excavate trench 300 mm beyond each side of pipe.  Backfill with cleaned, washed sand, hand placed, to a depth of 300 mm over top of pipe.  Hand tamp sand at completion of backfill.  Fill remainder of trench with Type 3 backfill.

### Above or below ground stainless steel.

#### Pipe material and fittings to be AISI type 316L.

#### Fittings to be push-fit type.

#### Fittings sealing rings to be EPDM except as indicated.

#### Fittings sealing rings for oil and petroleum service to be NBR.

#### Fittings sealing rings for heat resistance and resistance to oil, solvents and strong acids to be FPM.

# Execution

## Installation

### Install in accordance with Canadian Plumbing Code and local authority having jurisdiction and by certified journeyperson.

### Install above ground piping parallel and close to walls and ceilings to conserve headroom and space, and to grade as indicated.

### All vent piping serving corrosion resistant drainage piping distribution system to be corrosion resistant up to and through the roof penetrations.

### Provide fire stopping at drainage piping wall and floor penetrations through fire separations.

### Install and test to manufacturer’s recommendations.

### END OF SECTION