# General

## SUMMARY

### Section Includes:

#### Materials and installation for piping, fittings, equipment used in compressed air systems.

#### Sustainable requirements for construction and verification.

## Related Sections:

### Section 01 33 00 - Submittal Procedures.

### Section 01 45 00 - Quality Control.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 21 05 01 - Common Work Results for Mechanical.

### Section 23 05 16 - Expansion Fittings and Loops for HVAC Piping.

### Section 23 05 17 - Pipe Welding.

### Section 23 08 01 - Performance Verification of Mechanical Piping Systems.

### Section 23 08 02 - Cleaning and Start-Up of Mechanical Piping Systems.

## REFERENCES

### American Society of Mechanical Engineers (ASME)

#### ASME Boiler and Pressure Vessel Code Section VIII Pressure Vessels.

##### BPVC-VIII B BPVC Section VIII - Rules for Construction of Pressure Vessels Division 1.

##### BPVC-VIII-2 B, BPVC Section VIII - Rules for Construction of Pressure Vessels Division 2 - Alternative Rules.

##### BPVC-VIII-3 B, BPVC Section VIII - Rules for Construction of Pressure Vessels Division 3 - Alternative Rules High Press Vessels.

#### ASME B16.5, Pipe Flanges and Flanged Fittings.

#### ASME B16.11, Forged Fittings, Socket-Welding and Threaded.

### American Society for Testing and Materials International (ASTM)

#### ASTM A53/A53M, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless.

#### ASTM A181/A181M, Standard Specification for Carbon Steel Forgings for General Purpose Piping.

### Canadian Standards Association (CSA International)

#### CSA B51, Boiler, Pressure Vessel, and Pressure Piping Code.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

### Province of Newfoundland and Labrador

#### Boiler Pressure Vessel and Compressed Gas Regulations.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet for piping, fittings and equipment.

#### Submit WHMIS MSDS. Indicate VOC's for adhesive and solvents during application and curing.

### Shop Drawings:

#### Submit shop drawings to indicate project layout including layout, dimensions and extent of piping system.

##### Vertical and horizontal piping locations and elevations and connections details.

##### Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

##### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

##### Instructions: submit manufacturer's installation instructions.

##### Closeout Submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## QUALITY ASSURANCE

### Pre-Installation Meeting:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer's installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers Steel, Metal, Plastic waste in accordance with Waste Management Plan (WMP).

#### Handle and dispose of hazardous materials in accordance with Regional and Municipal regulations.

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

# Products

## AIR COMPRESSOR

### General: Two stage, air-cooled, V-belt driven, reciprocating or screw type with variable frequency drive, horizontal, tank-mounted.

### Valves: type ___.

### Motor: standard protected, premium efficiency.

### Control:

#### Manual control with H-0-A starter switch.

#### Pressure switch to cut out at 800 kPa and with minimum differential pressure.

#### Unloaders.

### Accessories: belt guard and pressure gauges.

### Air intakes: complete with bird screen, replaceable cartridge type intake filter and silencer.

### Capacity: ___ L/s of free air at 800 kPa at 1750 r/min.

### Vibration isolation: 95% minimum efficiency.

## AIR RECEIVER

### ___ mm diameter x ___ mm long horizontal tank: to CSA B51, ASME Section VIII and provincial regulations, for working gauge pressure of 800 kPa. Capacity: ___ L.

### Inlet and outlet connections: NPS ___.

### Accessories: adjustable pressure regulator, safety valve, 125 mm diameter gauge with pressure range of 0 to 1500 kPa, drain cock and automatic condensate trap.

### Provincial inspector's certificate and label and CRN.

### Finish: shop primed, ready for field painting.

## REFRIGERATED AIR DRYER

### Self-contained, hermetically sealed, complete with air cooled heat exchanger, compressor, automatic controls, moisture removal trap, wiring, piping and refrigerant charge.

### Inlet and outlet connections to be factory insulated.

### Capacity:

#### ___ L/s at an atmospheric dew point of minus 35 degrees C, ___ kPa and ___ degrees C inlet air at evaporator, 20 degrees C air to condenser.

#### Size to operate at ___% of time at design capacity.

### Electrical supply: ___ W, 120V, 1 phase, 60 cycle.

## CHEMICAL AIR DRYER

### Cartridge type , with bypass and valve.

## COMBINATION FILTER-REGULATOR

### Factory assembled, heavy-duty with mounting bracket and low pressure side relief valve.

### Maximum inlet pressure: ___ kPa.

### Operating temperature: minus 18 degrees C to plus 52 degrees C.

### Filter element: 5 micron. Bowls: polycarbonate.

### Pressure range in regulator: 34 kPa to 900 kPa.

### Gauge range: 0 kpa to 1500 kPa.

## PIPING

### Piping: to ASTM A53/A53M, schedule 80 seamless black steel, or tubular extruded aluminum with powder coated exterior rated for 1200 kPa.

### Fittings:

#### NPS2 and smaller: to ASME B16.11, schedule 80 steel, socket welded.

#### NPS2 1/2 and larger: to ASME B16.11, schedule 80 steel, butt or socket welded.

#### NPS3 and smaller: polyamide plastic or aluminum alloy compression type rated for 1200 kPa.

### Couplings: to ASME B16.11, socket welded or threaded half coupling type, or polyamide plastic or aluminum alloy compression type rated for 1200 kPa.

### Unions: 1000 kPa malleable iron with brass-to-iron ground seat, or polyamide plastic or aluminum alloy compression type rated for 1200 kPa.

### Dissimilar metal junctions: use dielectric unions.

### Flanges:

#### NPS2 and smaller: to ASME B16.5, forged steel, raised face and socket welded.

#### NPS2 1/2 and larger: to ASME B16.5, forged steel, raised face and slip-on or weld neck.

### Joints:

#### NPS2 and smaller: socket welded.

#### NPS2 1/2 and larger: butt welded.

#### NPS3 and smaller: compression type.

## BALL VALVES

### Three piece design or top entry for ease of in-line maintenance.

#### To ASTM A181/A181M, Class 70, carbon steel body socket welded or screwed ends, carbon steel ball and associated trim suitable for compressed air application.

#### To withstand 1034 kPa maximum pressure.

## COUPLERS/CONNECTORS

### Industrial interchange series, full-bore.

### Maximum inlet pressure: 1700 kPa.

### Valve seat: moulded nylon.

### Body: zinc plated steel.

### Threads: NPT.

# Execution

## MANUFACTURER'S INSTRUCTIONS

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## COMPRESSOR STATION

### Install on vibration isolators on housekeeping pad as indicated.

## REFRIGERATED AIR DRYER

### Install on three-valve bypass.

### Install tee connection after dryer for emergency connection to instrument control air system.

## COMPRESSED AIR LINE FILTER

### Install on discharge line from refrigerated air dryer.

## MAIN AIR PRESSURE REGULATORS

### Install at air compressor station.

### Install additional regulators on connections to equipment as indicated.

## COMPRESSED AIR PIPING CONNECTIONS AND INSTALLATION

### Install flexible connection in accordance with Section 23 05 16 - Expansion Fittings and Loops for HVAC Piping.

### Install shut-off valves at outlets, major branch lines and in locations as indicated.

### Install quick-coupler chucks and pressure gauges on drop pipes.

### Install unions to permit removal or replacement of equipment.

### Install tees in lieu of elbows at changes in direction of piping. Install plug in open ends of tees.

### Grade piping at 1% slope minimum.

### Install compressed air trap and pressure equalizing pipe at moisture collecting points. Drain pipe to nearest floor drain.

### Make branch connections from top of main or quick branch drop pipe if using aluminum piping system.

### Install compressed air trap at bottom of risers and at low points in mains, piped to nearest drain. Distance between drain points to be 30 m maximum.

### Provide drain from refrigerated air dryer.

### Weld steel piping in accordance with Section 23 05 17 - Pipe Welding and;

#### To ASME code and requirements of authority having jurisdiction.

#### Weld concealed and inaccessible piping regardless of size.

## FIELD QUALITY CONTROL

### Site Tests/Inspection:

#### Testing: pressure test in accordance with requirements of Section 21 05 01 - Common Work Results for Mechanical, for 4 h minimum, to 1100 kPa, with outlets closed and with compressor isolated from system. Pressure drop not to exceed 10 kPa.

### Manufacturer's Field Services:

#### Have manufacturer of products supplied under this Section review work involved in handling, installation/application, protection and cleaning of its products, and submit written reports, in acceptable format, to verify compliance of work with Contract.

#### Provide manufacturer's field services, consisting of product use recommendations and periodic site visits for inspection of product installation, in accordance with manufacturer's instructions.

#### Schedule site visits to review work at stages listed:

##### After delivery and storage of products, and when preparatory work on which work of this Section depends is complete, but before installation begins.

##### Twice during progress of work at 25% and 60% complete.

##### Upon completion of Work, after cleaning is carried out.

### Obtain reports within three (3) working days of review and submit immediately to Owner.

### Verification requirements include:

#### Materials and resources.

#### Storage and collection of recyclables.

#### Construction waste management.

#### Resource reuse.

#### Recycled content.

#### Local/regional materials.

#### Certified wood.

#### Low-emitting materials.

## CLEANING

### Refer to Section 23 08 01 - Performance Verification of Mechanical Piping Systems and Section 23 08 02 - Cleaning and Start-Up of Mechanical Piping System.

### Cleaning:  blow out piping to clean interior thoroughly of oil and foreign matter.

### Check entire installation is approved by authority having jurisdiction.

### Perform cleaning operations as specified in Section 23 08 02 - Cleaning and Start-Up of Mechanical Piping System and in accordance with manufacturer's recommendations.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION