# General

## summary

### Section includes:

#### The supply and installation of washroom fixtures and trim.

### Products installed but not supplied under this section as indicated elsewhere in the contract:

#### Install rough-in for equipment supplied by others, complete with valves on hot and cold water supplies, waste and vent.

#### Equipment installed by others.

##### Connect with unions.

#### Equipment not installed.

##### Capped for future connection by others.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

## References

### American National Standards Institute (ANSI)

#### ANSI 112-19.2, Ceramic Plumbing Fixtures.

### American National Standards Institute/national Sanitation Foundation (ANSI/NSF)

#### ANSI/NSF 61, Drinking Water System Components.

### Canadian Standards Association (CSA)

#### CAN/CSA-B45 Series, Plumbing Fixtures.

#### CAN/CSA-B125, Plumbing Fittings.

#### CAN/CSA-B651, Barrier-Free Design.

### Province of Newfoundland and Labrador Building Accessibility Act Regulations.

## submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:  Submit WHMIS SDS –Safety Data Sheets.

### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

### Indicate fixtures and trim:

#### Dimensions construction details, roughing-in dimensions.

#### Factory-set water consumption per flush at recommended pressure.

#### For water closets, urinals: minimum pressure required for flushing.

### Closeout Submittals:

#### Provide maintenance data including monitoring requirements for incorporation into manuals specified in Section 01 78 00 – Closeout Submittals.

#### Include:

##### Description of fixtures and trim, giving manufacturer’s name, type, model, year, capacity.

##### Details of operation, servicing, maintenance.

##### List of recommended spare parts.

## Quality Assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

## WARRANTY

### Provide a written guarantee, signed and issued in the name of the owner, against defective materials and workmanship for a period of one (1) year from the date of Substantial Completion.

# Products

## Manufactured Units

### Fixtures: manufacture in accordance with CAN/CSA-B45 series.

### Trim, fittings: manufacture in accordance with CAN/CSA-B125.

### Exposed plumbing brass to be chrome plated.

### Number, locations: Architectural drawings to govern.

### Fixtures to be product of one manufacturer and of same type.

### Trim to be product of one manufacturer and of same type.

## Water closets

| WC type | Mounting | Bowl | Flush valve | Flush tank | Barrier-free/Accessible |
| --- | --- | --- | --- | --- | --- |
|  | Wall | Floor | Elong | Reg | Exp’d | Conc’d |  |  |
| WC-1 | X |  | X |  | X |  |  |  |
| WC-2 | X |  | X |  | X |  |  | X |
| WC-3 |  | X | X |  |  |  | X |  |
| WC-4 |  | X | X |  |  |  | X | X |
| WC-5 | X |  | X |  |  | X |  |  |
| WC-6 | X |  | X |  |  | X |  | X |
| WC-7 |  | X | X |  |  |  | X 4.8 Lpf |  |
| WC-8 |  | X | X |  |  |  | X 4.8 Lpf | X |
| WC-9 |  | X | X |  |  |  | X Dual Flush |  |
| WC-10 |  | X | X |  |  |  | X Dual Flush | X |
| WC-11 |  | X | X |  |  | X |  |  |

#### WC-1: Wall-mounted, flush valve, top spud maximum 6 litres/flush.

##### Bowl: vitreous china, syphon jet, elongated rim, 50 mm ballpass trapway, NPS 1½ spud.

#### WC-2: Wall-mounted, flush valve, top spud maximum 6 litres/flush.

##### Bowl: vitreous china, syphon jet, elongated rim.

#### WC-3: Floor-mounted, flush tank.

##### Bowl: vitreous china, syphon jet, elongated rim, close-coupled combination, bowl and bolt caps.

##### Closet tank: vitreous china with tank liner, flapper type flush valve, 6 litres/flush.

#### WC-4: Floor-mounted, flush tank, for barrier-free/accessible, 6 litres/flush.

#### WC-5:  Wall-mounted, concealed flush valve, back inlet, 6 litres/flush, direct fed siphon jet flush action, 50 mm ballpass trapway, NPS 1½ inlet spud, elongated rim.

#### WC-6:  Wall-mounted, concealed flush valve, back inlet, 6 litres/flush, direct fed siphon jet flush action, 50 mm ballpass trapway, NPS 1½ spud, elongated rim for barrier-free/accessible.

#### WC-7: Floor-mounted, flush tank, bottom outlet, 4.8 Lpf, elongated siphon jet action bowl,  54 mm trapway minimum, bolt caps, anti-microbial surface, vitreous china, minimum 102 mm flush valve.

#### WC-8:  Floor-mounted, flush tank, bottom outlet, 4.8 Lpf, elongated siphon jet action bowl.  54 mm trapway minimum, bolt caps, anti-microbial surface, vitreous china, minimum 102 mm flush valve, 50 mm lift seal.

#### WC-9: Floor mounted flush tank bottom outlet, dual flush, 3.4/6.0 Lpf, 51 mm trapway.

#### WC-10: Floor mounted flush tank bottom outlet, dual flush, 3.4/6.0 Lpf, 51 mm trapway, 50 mm lift seal.

#### Alternative types 2, 4 and 6 may be the same as types 1, 3 and 5 with 50 mm lift seats to achieve barrier-free mounting height.

##### Top of seat to be between 400mm and 460mm from finished floor.

#### WC-11: floor mounted penal fixture:

##### Penal lavatory/water closet combination: 450 mm wide suicide resistant combination water closet and lavatory. Hemispherical cabinet design to reduce risk of fixture being used as a suicide device. Fixture to have the following features.

###### Fabricated from 2.0 mm Type 304 stainless steel.

###### D-shaped lavatory bowl (381 x 330 x 140 mm deep).

###### Pneumatically operated pushbutton valve.

###### Valve to comply with ANSI/NSF 61, Section 9, lead free requirements.

###### Provide hemispherical penal bubbler and hemispherical penal pushbutton.

###### Water-closet bowl housing to prohibit the attachment of objects.

###### Water-closet to be concealed blowout jet type with elongated bowl complete with self drainage flushing rim.

###### Integral contoured seat with a sanitary high polish finish.

###### Water-closet trap to pass 53 mm diameter ball.

###### Water-closet to conform with ANSI 112-19.2.

###### Cabinet interior shall be sound deadened with fire resistant materials.

###### Fixture to withstand loading of 1360 kg.

###### Fixture to be furnished with necessary fasteners for proper installation.

###### Water-closet to be floor mounted, wall outlet.

###### Unit to be left hand or right hand, as required to suit individual cell orientation.

###### Clean-out w/o-ring connecting metering valve.

###### Hot and cold air controlled metering valve.

###### 6 L flush valve.

###### 75 mm toilet p-trap.

###### Floor-trol anti-flood system.

###### Wall sleeve with 12 mm diameter steel bars.

###### Metal template.

### Water Closet Flush Valves

#### WCV-1 Water closet flush valve exposed, manual:

##### Quiet action, externally adjustable exposed diaphragm flush valve.

##### For water closets with NPS 1 ½ top spud.

##### Maximum 292 mm from centerline of valve inlet to top of water closet, except trap seal models which are maximum 298 mm.

##### Polished chrome plated finish.

##### Vandal resistant cover screw.

##### Metal “non hold open” oscillating handle.

##### NPS 1 FIP/Copper sweat inlet adaptor.

##### Adjustable 121 mm plus or minus 11 mm inlet/valve outlet centers.

##### Vacuum breaker.

##### 88 mm dia. cover tube and wall flange.

##### Renewable seat.

##### Chloramine resistant diaphragm attached to guide with forged metal retainer.

##### Spud flange and concealed spud nut.

##### Pressure loss check angle stop with protecting cap.

##### 6 litre Factory set flush – field adjustable.

#### WCV-2 Water closet flush valve, concealed, manual:

##### CSA certified.

##### Complies to ASSE Standard 1037.

##### Oscillating Lever Handle (non hold open) ADA compliant and meets Handicapped Accessibility Standard ANSI 117.1.

##### IAPMO listed.

##### Quiet action, concealed diaphragm flush valve.

##### For wall hung NPS 1½ back inlet water closet.

##### Renewable seat.

##### Vandal resistant handle control can easily be located and installed anywhere within 6m of flush valve.

##### Standard flush valve will install on all walls zero to 343 mm thick.

##### Adjustable 121 mm plus or minus 11mm inlet/valve outlet centers.

##### Vacuum breaker.

##### Wheel handle angle pressure loss check stop 1 FIP/copper sweat inlet adaptor.

##### Polished chrome plated finish on exposed t.rim

##### 6 litre factory set Flush – Field Adjustable.

#### WCV-3 Water closet flush valve, concealed, electronic:

##### CSA certified.

##### ADA compliant and meets Handicapped Accessibility Standard ANSI 117.1.

##### Complies to ASSE standard 1037.

##### IAMPO listed.

##### Infrared electronic activation.

##### 355 mm stainless steel cover with integral sensor.

##### Recessed mounting components assembled with flush valve in 305mm frame.

##### Preset blocking time, built-in activation delay.

##### Electronic manual override.

##### Solenoid operation valve.

##### 8 second blocking time.

##### 4 second activation delay.

##### Adjustable flush volume with adjustment screw.

##### Selectable sensing distance 610 to 1400 mm in 200 mm increments. Factory set at 1000 mm.

##### 24 hour courtesy flush, factory set to off.

### Water Closet Seats and Backrests:

#### Seat:  white, elongated, open front, molded solid plastic, less cover, stainless steel check hinges, stainless steel or solid brass insert post. For handicapped closets include cover if back rest not provided by architect.

## Urinals

#### U-1: Wall-mounted, 3 litres flush, exposed flush valve, top spud.

##### Urinal: vitreous china, washout type, integral flushing rim, extended shields, integral trap, removable stainless steel strainer, back outlet for concealed arm carrier.

#### U-2: Wall-mounted, 3 litres flush, exposed flush valve, back inlet.

##### Urinal: vitreous china, washout type, integral flushing rim, extended shields, integral trap, removable stainless steel strainer, back outlet for concealed arm carrier.

#### U-3: Wall-mounted, back spud, 1.9L flush

##### Urinal: low consumption, integral flushing mechanism, elongated 356mm rim from finished wall, flushing rim, washout flush action, integral extended sides, wall hangers, 50mm NPTF outlet connection, cover and mounting kit, plug-in power supply 120  VAC, 60 HZ, 5VDC, 500 ma output.

#### Urinal Flush Valves

##### UFV-1 Urinal flush valve, exposed, manual:

###### Quiet action, exposed diaphragm flush valve.

###### For flushing urinals with NPS 3/4 top spud.

###### Maximum 330 mm from centerline of valve inlet to top of urinal except trap seal models which are maximum 315 mm.

###### External water conserving flush volume adjustment.

###### Polished chrome plated finish.

###### Vandal resistant cover screw.

###### Metal “not hold open” oscillating handle.

###### NPS 1 FIP/NPS ¾ copper sweat inlet adaptor.

###### Adjustable 121 mm plus or minus 11 mm inlet/valve outlet centers.

###### Vacuum beaker.

###### 38 mm dia. cover tube and wall flange.

###### Renewable seat.

###### Chloramine resistant diaphragm attached to guide with forged metal retainer.

###### Spud flange and concealed spud nut.

###### Pressure loss check angle stop with protecting cap.

###### Factory set for 2.7 L flush-field adjustable.

##### UFV-2 Urinal Flush Valve, concealed, manual:

###### CSA certified.

###### Complies to ASSE Standard 1037.

###### Oscillating Lever Handles (non hold open) ADA compliant and meets Handicapped Accessibility Standard ANSI 117.1.

###### IAPMO listed.

###### Quiet action, concealed diaphragm flush valve.

###### For wall hung NPS ¾ back inlet urinal fixture.

###### Renewable seat.

###### Chloramine resistant diaphragm attached to guide with forged metal retainer.

###### External water conserving flush volume adjustment.

###### Vandal resistant handle control can easily be located and installed anywhere within 6m of flush valve.

###### Standard flush valve will install on all walls zero to 343 mm thick.

###### 1 FIP/ ¾ copper sweat inlet adaptor.

###### Adjustable 121 mm plus or minus 11 mm inlet/valve outlet centers.

###### Wheel handle angle pressure loss check stop.

###### Vacuum breaker.

###### Polished chrome plated finish on exposed trim.

###### Factory set For 2.7 litre flush.

##### UFV-3 Urinal Electronic Flush Valves for Public Washrooms and as indicated.

###### CSA certified.

###### ADA compliant and meets Handicapped Accessibility Standard ANSI 117.1.

###### Complies to ASSE standard 1037.

###### IAMPO listed.

###### Infrared electronic activation.

###### 355 mm stainless steel cover with integral sensor.

###### Recessed mounting components assembled with flush valve in 305mm frame.

###### Preset blocking time, built-in activation delay.

###### Electronic manual override.

###### Solenoid operation valve.

###### 8 second blocking time.

###### 4 second activation delay.

###### Adjustable flush volume with adjustment screw.

###### Selectable sensing distance 610 to 1400 mm in 200 mm increments. Factory set at 1000 mm.

###### 24 hour courtesy flush, factory set to off.

## Washroom Lavatories

#### L-1: Wall-hung, integral back:

Vitreous china, with splash lip, soap depressions, supply openings on 100 mm centres, front overflow, for concealed arm carrier. Size: 500 x 450 mm.

#### L-2	Counter-top:

##### Vitreous China, self-rimming, with front overflow, soap depressions, gasket, swivel clamps, semi-oval or rectangular bowl, supply openings on 100 mm centres.  Sizes: 518 X 432 mm outside, 400 X 250 X 180 mm nominal inside.

#### L-3	Wall-hung, for accessible/barrier –free.

##### Vitreous china, low shelf, with integral back, contoured front, shallow front basin, front overflow, soap depressions, supply openings on 300 mm centres, concealed arm carrier.  Sizes: 675 X 500 mm.

#### L.-4	Counter-top:

##### Stainless steel grade 18-8 type 304, self-rimming, radius bowl corners, hold down clamping, hole drilling to suit faucet, undercoated, integral overflow, mirror finish rim, satin finish bowl, 540 mm X 427 mm X 152 mm, 100 mm centres.

#### Washroom Lavatory Trim.

#### LT-1

- 102 mm two handle, cast brass centerset.

- Polished chrome plated finish.

- Heavy duty brass compression structures.

- 90% flow with first ¼ turn of operation, 1800.

- Positive shutoff even in poor water conditions.

- Metal hold-down package.

- Centerset with cast open grid strainer, no pop-up hole, 2-hole installation.

- Non-aerator 1.9 L/min. vandal resistant.

- 102 mm blade handles, sanitary hood, metal color indexed vandal resistant screws.

#### LT-2

- Single handle kitchen deck faucets for exposed mounting on single, three and four hole sinks.

- Solid brass fabricated body.

- 203 mm long spout swings 3600.

- Vandal resistant aerator, 8.3 L/min.

- Vandal resistant 152 mm elbow handle. Red/blue colored graphics indicate hot/cold temperature.

- Control mechanism to be of the rotating stainless steel ball type with replaceable non-metallic seats operating in stainless steel lined sockets.

- Control handle to return to neutral position when valve is turned off.

- Adjustable handle limit stop.

#### LT-3 Wheelchair supply fitting with cast brass gooseneck spout, aerator, waste fitting: open grid strainer.

- Hard wire.

- Infrared electronic handwash system.

- Chrome plated one piece cast main body with integral sensor.

- Field adjustable water resistant program controller.

- Backlit indicator adjustment buttons.

- Unit retains adjusted settings in event of power failure.

- Chrome plated forged brass solenoid valve with Y strainer cleanout.

- Water flows when sensor is activated.

- Water flow stops at the selected run-on time after user removes hands from sensing zone.

- Run on time selections are 0 to 8 seconds or 1 to 8 minutes for scrub-up applications. Factory set to 8 seconds.

- Blocking time between uses has selectable range of 0 to 8 seconds.  Factory set to 0 seconds.

- Auto shut-off feature that is selectable between 1 to 9 minutes.  Factory set to 1 minute.

- Metered program mode with selection of 7 to 240 seconds of continuous operation.

- Adjustable sensing distance from 76 mm to 356 mm factory set to 229 mm sensor ranges are +/- 25 mm subject to environmental conditions based on Kodak grey card R27 90% reflective.

- 110 to 24 VAC Transformer for hardwire models.

- Integrated sensor.

- Vandal resistant 1.9L/min aerating outlet.

- Single hole deckmount highrise spout with integral sensor in base.

- Factory assembled in recessed mounting 250 mm metal box with stainless steel cover – includes mechanical mixing valve with thermostatic limit stop.

#### LT-4 Washroom Lavatory Electronic Trim for Public Washrooms and as indicated.

- Hard wire.

- 102 mm electronic faucet.

- Cast one-piece body with integral waterproof sensor and connector.

- DMD self-adaptive technology no external adjustments required.

- Serviceable filter screen upstream of solenoid valve.

- Metal hold-down package.

- Hands free (touchless) operation.

- Water flows when sensor is activated.

- Water flow stops upon de-activation of sensor.

- Sensing zone approximately 178 mm.

- Pre-set 45 second maximum run time.

- Will reset once obstruction is removed.

- 110 to 24 VAC transformer.

- Chrome finish.

- 102 mm cast lavatory faucet.

- Vandal resistant 1.9L/min.) flow control non-aerating spray outlet.

- Factory assembled in recessed mounting 250 mm metal box with stainless steel cover- includes mechanical mixing valve with thermostatic limit stop.

## Fixture piping

#### Hot and cold water supplies to fixtures:

##### Chrome plated flexible supply pipes with screwdriver stop, reducers, escutcheon.

#### Waste:

##### Brass P trap with cleanout on fixtures not having integral trap.

##### Chrome plated in exposed places.

## Chair carriers.

#### Factory manufactured floor-mounted carrier systems for wall-mounted fixtures.

# Execution

## Installation

### Mounting heights:

#### Standard: to comply with manufacturer's recommendations unless otherwise indicated or specified.

#### Wall-hung fixtures: as indicated, measured from finished floor.

#### For barrier-free washrooms: to comply with most stringent of either NBCC or CAN/CSA B651, or Provincial Building Accessibility Act and Regulations.

## Adjusting

### Conform to water conservation requirements specified this section.

#### Adjustments.

##### Adjust water flow rate to design flow rates.

##### Adjust pressure to fixtures to ensure no splashing at maximum pressures.

##### Adjust flush valves to suit actual site conditions.

##### Adjust urinal flush timing mechanisms.

##### Automatic flush valves for urinals and waterclosets: set controls to prevent unnecessary flush cycles during silent hours.

#### Checks.

##### Water closets, urinals: flushing action.

##### Aerators: operation, cleanliness.

##### Vacuum breakers, backflow preventers: operation under all conditions.

#### Thermostatic controls.

##### Verify temperature settings, operation of control, limit and safety controls.

END OF SECTION