# General

## summary

### Section includes:

#### The supply and installation of washroom fixtures and trim.

### Products installed but not supplied under this section:

#### Install rough-in for equipment supplied by others, complete with valves on hot and cold water supplies, waste and vent.

#### Equipment installed by others.

##### Connect with unions.

#### Equipment not installed.

##### Valved and capped for future connection by others.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

## References

### Air Conditioning and Refrigeration Institute (ARI)

#### ARI 1010, Self-Contained, Mechanically Refrigerated Drinking-Water Coolers.

### Canadian Standards Association (CSA)

#### CAN/CSA-B45 Series, CSA Standards on Plumbing Fixtures.

#### CAN/CSA-B125, Plumbing Fittings.

#### CAN/CSA-B651, Barrier-Free Design.

### Province of Newfoundland and Labrador Building Accessibility Regulations.

## submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:  Submit WHMIS SDS – Safety Data Sheets.

### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

### Indicate for all fixtures:

#### Dimensions, construction details, roughing-in dimensions.

### Closeout Submittals:

#### Provide maintenance data including monitoring requirements for incorporation into manuals specified in Section 01 78 00 – Closeout Submittals.

#### Include:

##### Description of fixtures and trim, giving manufacturer’s name, type, model, year, capacity.

##### Details of operation, servicing, maintenance.

##### List of recommended spare parts.

## Quality Assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

## WARRANTY

### Provide a written guarantee, signed and issued in the name of the owner, against defective materials and workmanship for a period of one (1) year from the date of Substantial Completion.

# Products

## Manufactured Units

### Fixtures: manufacture in accordance with CAN/CSA-B45 series.

### Trim, fittings: manufacture in accordance with CAN/CSA-B125.

### Exposed plumbing brass to be chrome plated.

### Number, locations: Architectural drawings to govern.

## Drinking fountains

### DF-1:  Recessed with elevated bubbler base, integral strainer, wall screws with washers and cap nuts, 1.2 mm Type 304 stainless steel no. 4 satin finish,front mounted push button valve, meets Newfoundland and Labrador Buildings Accessibility Act and Regulations for side approach.

#### Trim chrome plated: angle stream anti-squirt bubbler with automatic stream regulator, self-closing valve, screwdriver stop, waste tailpiece, filter, chrome plated waste strainer

### DF-2 : Wall-hung barrier free dual height 1.2 mm stainless steel Type 304, No. 4 satin finish, stainless steel back panel, integral chrome plated strainer, wall hanger.

#### Trim: chrome plated angle stream anti-squirt bubbler with in line strainer and automatic stream regulator, push button with two one piece fountains, with rounded bowls, self-closing valve, screwdriver stop, waste tailpiece, and access cover.

### DF-3: Self-contained, wall mounted water cooler with bottle filling station, 1.2 mm stainless steel Type 304, No. 4 satin finish, light touch front and side push bar actuation with raised letters for visually impaired.

#### Trim chrome plated: angle stream anti-squirt bubbler with automatic stream regulator, self-closing valve, screwdriver stop, waste tailpiece, filter, chrome plated waste strainer.

#### Unit to include Green Counter displaying the count of plastic bottles saved from landfill.

#### Bottle filler shall include electric sensor for no-touch activation with automatic 20-second shut off timer.

#### Capacity: 30 L/h at 32°C ambient air, cooled to 10°C. In accordance with ARI 1010.

## Refrigerated water coolers

### RWC-1: Wall-mounted barrier free.

#### Refrigeration system: packaged hermetic R134a unit with pre-cooler, insulated double wall chiller, storage tank, air-cooled condenser, thermostatically controlled.

#### Capacity: 30 L/h from 27°C to 10°C, with 32°C ambient air. In accordance with ARI 1010.

#### Cabinet: two receptors dual height type 304 stainless steel, No. 4 satin finish, one piece rectangular bowls with rounded corners, integral back, 60 micron mesh strainer, access panel and grille, elevated bubbler base, chrome plated waste strainer.

#### Bubbler: chrome plated pushbutton operated, self-regulating, angle stream, squirt-proof, with nozzle and guard.

#### Electrical: grounded electrical cord with plug: 120 V, 60 Hz. CSA certified.

## FIXTURE PIPING

### Cold water supplies to each fixture:

#### Shut off valve in supply pipes each with handwheel stop, reducers, escutcheon.

### Waste:

#### Brass P trap with cleanout on each fixture not having integral trap.

# Execution

## Installation

### Mounting heights:

#### Standard: to comply with manufacturer's recommendations unless otherwise indicated or specified.

#### Wall-hung fixtures: measured from finished floor.

#### Physically handicapped: to comply with most stringent of either NBCC, CAN/CSA B651 or Provincial Building Accessibility Act and Regulations.

### Drinking fountains and water coolers:

#### In accordance with ARI 1010.

## Adjusting

### Conform to water conservation requirements specified this section.

### Adjustments.

#### Adjust water flow rate to design flow rates.

#### Adjust water cooler, drinking fountain flow stream to ensure no spillage.

### Checks.

#### Refrigerated water coolers: operation, temperature settings.

#### Thermostatic controls.  Verify temperature settings, operation of control, limit and safety controls.

#### Report checks and verifications in Commissioning Manual.

END OF SECTION