# General

## SUMMARY

### Use of HVAC systems during construction.

## Related Sections

### Section 01 51 00 - Temporary Utilities.

## Use of Systems

### Use of new and/or existing permanent heating and/or ventilating systems for supplying temporary heat or ventilation is permitted only under the following conditions:

#### Entire system is complete, pressure tested, cleaned, flushed out.

#### Specified water treatment system has been commissioned, water treatment is being continuously monitored.

#### Building has been closed in, areas to be heated/ventilated are clean and will not thereafter be subjected to dust-producing processes.

#### There is no possibility of damage from any cause.

#### Supply ventilation systems are protected by 60 % filters, which shall be inspected daily, changed every week or more frequently as required.

#### Return systems have approved filters over all openings, inlets, outlets.

#### All systems will be:

##### Operated as per manufacturer's recommendations or instructions.

##### Operated by Contractor.

##### Monitored continuously by Contractor.

#### Warranties and guarantees are not thereby relaxed.

#### Regular preventive and all other manufacturers recommended maintenance routines are performed by Contractor at his own expense and under supervision of Owner.

#### Refurbish entire system before static completion; clean internally and externally, restore to "as- new" condition, and replace filters in air systems.

### Filters specified in this section are over and above those specified in other sections of this project.

### Exhaust systems are not included in any approvals for temporary heating ventilation.

# Products (NOT used)

# Execution (NOT used)

END OF SECTION