# General

## summary

### Section Includes:

#### Electrical motors, drives and guards for mechanical equipment and systems.

#### Supplier and installer responsibility indicated in Motor, Control and Equipment Schedule on electrical drawings and related mechanical responsibility is indicated on Mechanical Equipment Schedule on mechanical drawings.

#### Control wiring and conduit specified in Division 26. Control wiring 50V or less for systems specified in Division 21, 22, 23 and 25 is by Division 25.

## Related Sections:

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

## References

### American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE)

#### ASHRAE 90.1, Energy Standard for Buildings Except Low-Rise Residential Buildings (IESNA cosponsored; ANSI approved; Continuous Maintenance Standard).

### National Energy Code for Buildings (NECB).

### Health Canada/Workplace Hazardous Materials Information System (WHMIS).

#### Safety Data Sheets (SDS).

### National Electrical Manufacturers Association (NEMA).

## submittals

### Submittals: in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures.  Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

#### Shop Drawings:   Submit drawings stamped and signed for approval by Owner.

#### Quality Control: in accordance with Section 01 45 00 - Quality Control.

##### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

##### Instructions: submit manufacturer's installation instructions.

###### Owner will make available one (1) copy of systems supplier's installation instructions.

#### Closeout Submittals

##### Provide maintenance data for motors, drives and guards for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## quality assurance

### Regulatory Requirements: work to be performed in compliance with Canadian Environmental Protection Act (CEPA), Canadian Environmental Assessment Agency (CEAA), Transportation of Dangerous Goods Act (TDGA) and applicable Provincial regulations.

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## General

### Motors to be premium efficiency, in accordance with local hydro company standards and the requirements of ASHRAE 90.1.

## Motors

### Provide motors for mechanical equipment as specified.

### Motors under  1/2 HP : speed as indicated, continuous duty, built-in overload protection, resilient mount, single phase, 120 V, unless otherwise specified or indicated.

### Motors 1/2 HP and larger: NEMA, Class B, 1.15 service factor, squirrel cage induction, premium efficiency, speed as indicated, continuous duty, enclosure as indicated, ball bearing, maximum temperature rise 40o C, 3 phase, 575 V, unless otherwise indicated, for inverted duty for variable frequency drives.

## Temporary Motors

### If delivery of specified motor will delay completion or commissioning work, install motor approved by Owner for temporary use. Work will only be accepted when specified motor is installed.

## Belt Drives

### Fit reinforced belts in sheave matched to drive. Multiple belts to be matched sets.

### Use cast iron or steel sheaves secured to shafts with removable keys unless otherwise specified.

### For motors under 10 HP: standard adjustable pitch drive sheaves, having plus or minus 10% range. Use mid-position of range for specified r/min.

### For motors 10 HP and over: sheave with split tapered bushing and keyway having fixed pitch unless specifically required for item concerned. Provide sheave of correct size to suit balancing.

### Correct size of sheave to be determined during commissioning.

### Minimum drive rating: 1.5 times nameplate rating on motor. Keep overhung loads within manufacturer's design requirements on prime mover shafts.

### Motor slide rail adjustment plates to allow for centre line adjustment.

### Supply one set of spare belts for each set installed in accordance with Section 01 78 00 – Closeout Submittals.

## Drive Guards

### Provide guards for unprotected drives.

### Guards for belt drives;

#### Expanded metal screen welded to steel frame.

#### Minimum 1.2 mm thick sheet metal tops and bottoms.

#### 38 mm dia holes on both shaft centres for insertion of tachometer.

#### Removable for servicing.

### Provide means to permit lubrication and use of test instruments with guards in place.

### Install belt guards to allow movement of motors for adjusting belt tension.

### Guard for flexible coupling:

#### "U" shaped, minimum 1.6 mm thick galvanized mild steel.

#### Securely fasten in place.

#### Removable for servicing.

### Unprotected fan inlets or outlets:

#### Wire or expanded metal screen, galvanized, 19 mm mesh.

#### Net free area of guard: not less than 80% of fan openings.

#### Securely fasten in place.

#### Removable for servicing.

# Execution

## MANUFACTURER'S INSTRUCTIONS

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## INSTALLATION

### Fasten securely in place.

### Make removable for servicing, easily returned into, and positively in position.

## FIELD QUALITY CONTROL

### Site Tests: conduct following tests in accordance with Section 01 45 00 - Quality Control and submit report as described in PART 1 - SUBMITTALS.

#### As specified in other sections of this specification.

### Manufacturer's Field Services:

#### Obtain written report from manufacturer verifying compliance of Work, in handling, installing, applying, protecting and cleaning of product and submit Manufacturer's Field Reports as described in PART 1 - SUBMITTALS.

#### Provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions.

#### Schedule site visits, to review Work, as directed in PART 1 - QUALITY ASSURANCE.

## CLEANING

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION