# GENERAL

## SECTION INCLUDES

### Materials and installation for flexible connections, expansion joints, anchors and guides for building services piping.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 35 29.06 - Health and Safety Requirements.

### Section 01 74 21 - Construction/Demolition Waste Management And Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 03 20 00 - Concrete Reinforcing.

### Section 03 30 00 - Cast-in-Place Concrete.

### Section 03 30 00.01 - Cast-in-Place - Short Form.

### Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems.

### Section 23 08 01 - Performance Verification Mechanical Piping Systems.

## REFERENCES

### American Society for Testing and Materials International, (ASTM).

#### ASTM A 53/A53M, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

#### ASTM A 105/A105M, Standard Specification for Carbon Steel Forgings, for Piping Applications.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Submit product data and indicate for items as applicable:

#### Manufacturer, model number, line contents, pressure and temperature rating.

#### Movement handled, axial, lateral, angular and the amounts of each.

#### Nominal size and dimensions including details of construction and assembly.

### Submit maintenance data in accordance with Section 01 78 00 - Closeout Submittals.

### Data to include:

#### Servicing requirements, including special requirements, stuffing box packing, lubrication and recommended procedures.

## HEALTH AND SAFETY

### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## WASTE MANAGEMENT AND DISPOSAL

### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect, separate and place in designated containers for reuse and recycling, paper, plastic, polystyrene, corrugated cardboard packaging, steel, metal, in accordance with Waste Management Plan.

### Unused sealant materials must not be disposed of into sewer system, into streams, lakes, onto ground or in other location where it will pose health or environmental hazard.

### Fold up metal banding, flatten and place in designated area for recycling.

# PRODUCTS

## SLIP TYPE EXPANSION JOINTS

### Application: for axial pipe movement, as indicated.

### Repacking: under full line pressure.

### Body and packing housings: Class 150, 1MPa or Class 300, 2MPa carbon steel pipe to ASTM A53/A53M, Grade B. Wall thickness to match pipe with raised face slip-on or weld neck flanges to match pipe.

### Slip or traverse sleeves: carbon steel pipe to ASTM A53/A53M, Grade B, hard chrome plated.

### Anchor base: construction steel, welded to body.

### Guides (internal and external): embody into packing housing with concentric alignment of slip or traverse sleeve with packing housing.

### Extension limit stop: stainless steel, to prevent over-extension with accessible and removable pins.

### Packing rings: 6.0 minimum, PTFE or graphite impregnated non-asbestos.

### Thermal plastic packing: PTFE or graphite impregnated non-asbestos slug supplied loose.

### Lubricating fittings: pet cocks with grease nipple.

### Plunger body and plunger:

#### Plunger body: heavy wall carbon steel welded to body.

#### Plunger: carbon steel with hex head for use with socket wrench.

### Lubricant: to manufacturer's recommendations.

### Lubricant gun: complete with hose assembly.

### Drip connection: 20 MPa forged steel to ASTM A 105/A105M. Include half coupling with drain plug.

## BELLOWS TYPE EXPANSION JOINTS

### For axial, lateral or angular movements, as indicated.

### Maximum operating pressure: same as pipe rating.

### Maximum operating temperature: same as pipe rating.

### Type A: controlled free flexing, factory tested to 1 ½ times maximum working pressure. Furnish test certificates.

### Type B: externally pressurized, constant volume, pressure balanced, designed to eliminate pressure thrust, factory tested to 1 ½ times maximum working pressure. Furnish test certificates.

### Bellows:

#### Multiple bellows, hydraulically formed, single or two ply, austenitic stainless steel, monel, or inconel for specified fluid, pressure and temperature, water treatment and pipeline cleaning procedures.

### Reinforcing or control rings:

#### 2 piece nickel iron.

### Ends:

#### Raised face, slip-on or weld neck flanges to match pipe.

### Liner:

#### Austenitic stainless steel in direction of flow.

### Shroud:

#### Carbon steel, painted.

## FLEXIBLE CONNECTION

### Application: to suit motion as indicated.

### Minimum length in accordance with manufacturer's recommendations to suit offset

### Inner hose: bronze or stainless steel corrugated.

### Braided wire mesh bronze or stainless steel outer jacket.

### Diameter and type of end connection: threaded or flanged, same as pipe joint for the pipe size.

### Operating conditions:

#### Working pressure: 1034 kPa.

#### Working temperature: to match system requirements.

#### To match system requirements.

## ANCHORS AND GUIDES

### Anchors:

#### Provide as indicated.

#### Concrete: to Section 03 30 00 - Cast-in-Place.

#### Reinforcement: to Section 03 20 00 - Concrete Reinforcing.

### Alignment guides:

#### Provide as indicated.

#### To accommodate specified thickness of insulation.

#### Vapour barriers, jackets to remain uninterrupted.

# EXECUTION

## INSTALLATION

### Install expansion joints with cold setting. Make record of cold settings.

### Install expansion joints and flexible connections in accordance with manufacturer's instructions.

### Install pipe anchors and guides as indicated. Anchors to withstand 150 % of axial thrust.

## CLEANING AND START-UP

### In accordance with Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems.

## PERFORMANCE VERIFICATION

### In accordance with Section 23 08 01 - Performance Verification: Mechanical Piping Systems.

END OF SECTION