# General

## RELATED SECTIONS

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

### Section 23 21 13.02 - Hydronic Systems:  Steel

## REFERENCES

### American National Standards Institute/American Society of Mechanical Engineers. (ANSI/ASME)

#### ANSI/ASME B31.1, Power Piping.

#### ANSI/ASME B31.3, Process Piping.

#### ANSI/ASME B31.5, Refrigeration Piping and Heat Transfer Components.

#### ANSI/ASME B31.9 Building Services.

#### ANSI/ASME Boiler and Pressure Vessel Code

##### Section I: Power Boilers.

##### Section V: Nondestructive Examination.

##### Section IX: Welding and Brazing Qualifications.

### American National Standards Institute/American Water Works Association (ANSI/AWWA)

#### ANSI/AWWA C206, Field Welding of Steel Water Pipe.

### American Welding Society (AWS)

#### AWS C1.1, Recommended Practices for Resistance Welding.

#### AWS Z49.1, Safety Welding, Cutting and Allied Process.

#### AWS W1, Welding Inspection Handbook.

### Canadian General Standards Board

#### CAN/CGSB-48.2, Spot Radiography of Welded Butt Joints in Ferrous Materials.

### Canadian Standards Association (CSA International)

#### CSA W47.2, Certification of Companies for Fusion Welding of Aluminum.

#### CSA W48 series, Filler Metals and Allied Materials for Metal Arc Welding.

#### CSA B51, Boiler, Pressure Vessel and Pressure Piping Code.

#### CSA B52 Mechanical Refrigeration Code.

#### CSA W117.2, Safety in Welding, Cutting and Allied Processes.

#### CSA W178.1, Certification of Welding Inspection Organizations.

#### CSA W178.2, Certification of Welding Inspectors.

### Provincial regulations:  Boiler, Pressure Vessel and Compressed Gas Regulations.

## QUALIFICATIONS

### Welders

#### Welding qualifications in accordance with CSA B51.

#### Use qualified and licensed welders possessing certificate for each procedure performed from authority having jurisdiction.

#### Furnish welder's qualifications to Owner.

#### Each welder to possess identification symbol issued by authority having jurisdiction.

#### Certification of companies for fusion welding of aluminum in accordance with CSA W47.2.

### Inspectors

#### Inspectors qualified to CSA W178.2.

## QUALITY ASSURANCE

### Registration of welding procedures in accordance with CSA B51, CSA B52 and provincial regulations.

### Copy of welding procedures available for inspection.

### Safety in welding, cutting and allied processes in accordance with CSA-W117.2.

## waste management and disposal

### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction / Demolition Waste Management and Disposal, and with the Waste Reduction Workplan.

### Remove from site and dispose of all packaging materials at appropriate recycling facilities.

### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

# Products

## ELECTRODES

### Electrodes: in accordance with CSA W48 Series.

# Execution

## WORKMANSHIP

### Welding: in accordance with ANSI/ASME B31.1 B31.3, B 31.5, B31.9, ANSI/ASME Boiler and Pressure Vessel Code, Sections I and IX and ANSI/AWWA C206, using procedures conforming to AWS C1.1, and special procedures specified elsewhere in Mechanical Division and applicable requirements of provincial authority having jurisdiction.

## INSTALLATION REQUIREMENTS

### Identify each weld with welder's identification symbol.

### Backing rings:

#### Where used, fit to minimize gaps between ring and pipe bore.

#### Do not install at orifice flanges.

### Fittings:

#### NPS 2 and smaller: install welding type sockets.

#### Branch connections: install welding tees or forged branch outlet fittings.

## INSPECTION AND TESTS - GENERAL REQUIREMENTS

### Review weld quality requirements and defect limits of applicable codes and standards with Owner before work is started.

### Formulate "Inspection and Test Plan" in co-operation with Owner.

### Do not conceal welds until they have been inspected, tested and approved by inspector.

### Provide for inspector to visually inspect welds during early stages of welding procedures in accordance with Welding Inspection Handbook. Repair or replace defects as required by codes and as specified.

## SPECIALIST EXAMINATIONS AND TESTS

### General

#### Perform examinations and tests by specialist engaged by contractor, qualified in accordance with CSA W178.1 and CSA W178.2 and approved by Owner.

#### To ANSI/ASME Boiler and Pressure Vessels Code, Section V, CSA B51 and requirements of authority having jurisdiction.

#### Inspect and test welds in accordance with "Inspection and Test Plan" by non-destructive visual examination and magnetic particle (hereinafter referred to as "particle") tests and/or spot or full gamma ray radiographic (hereinafter referred to as "radiography") tests. As per applicable reference standard or as specified.

### Hydrostatically test welds to requirements of ANSI/ASME B31.1.

### Visual examinations: include entire circumference of weld externally and wherever possible internally.

### Failure of visual examinations:

#### Upon failure of welds by visual examination, perform additional testing as directed by Owner of total of up to 10 % of welds, selected at random by Owner by radiographic tests.

### Full radiographic tests for piping systems.

#### Spot radiography to CAN/CGSB-48.2.

##### Conduct spot radiographic tests of up to 10% of welds, selected at random by Owner from welds which would be most difficult to repair in event of failure after system is operational.

#### Radiographic film:

##### Identify each radiographic film with date, location, name of welder, and submit to Owner. Replace film if rejected because of poor quality.

#### Interpretation of radiographic films:

##### By qualified radiographer.

#### Failure of radiographic tests:

##### Extend tests to welds by welder responsible when those welds fail tests.

### Magnetic particle tests for piping systems as indicated.

## DEFECTS CAUSING REJECTION

### As described in ANSI/ASME B31.1 and ANSI/ASME Boiler and Pressure Vessels Code.

### In addition, chilled water systems below 1000 kPa:

#### Undercutting greater than 0.8 mm adjacent to cover bead on outside of pipe.

#### Undercutting greater than 0.8 mm adjacent to root bead on inside of pipe.

#### Undercutting greater than 0.8 mm at combination of internal surface and external surface.

#### Incomplete penetration and incomplete fusion greater than total length of 38 mm in 1500 mm length of weld depth of such defects being greater than 0.8 mm.

#### Repair cracks and defects in excess of 0.8 mm in depth.

#### Repair defects whose depth cannot be determined accurately on basis of visual examination or radiographic particle tests.

## REPAIR OF WELDS WHICH FAILED TESTS

### Re-inspect and re-test repaired or re-worked welds at Contractor's expense.

END OF SECTION