# General

## section INCLUDES

### Materials and installation for thermometers and pressure gauges in piping systems.

## related sections

### Section 01 33 00 – Submittal Procedures

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 23 05 23.01 – Valves - Bronze

### Section 23 05 53.01 – Mechanical Identification

## References

### American Society of Mechanical Engineers (ASME)

#### ASME B40.100, Pressure Gauges and Gauge Attachments.

#### ASME B40.200, Thermometers, Direct Reading and Remote Reading.

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-14.4, Thermometers, Liquid-in-Glass, Self Indicating, Commercial/Industrial Type.

#### CAN/CGSB-14.5, Thermometers, Bimetallic, Self-Indicating, Commercial/Industrial Type.

## submittals

### Submit in accordance with Section 01 33 00 – Submittal Procedures.

### Submit shop drawings and product data.

### Submit manufacturer’s product data for following items:

#### Thermometers

#### Pressure Gauges

#### Ball Valves

#### Syphons

#### Wells

## Health and safety

### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## Waste management and disposal

### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Collect, separate and place in designated containers for reuse and recycling, paper, plastic, polystyrene, corrugated cardboard packaging, steel, metal, in accordance with Waste Management Plan.

### Fold up metal banding, flatten and place in designated area for recycling.

### Place materials defined as hazardous or toxic waste in designated containers.

### Ensure emptied containers are sealed, labelled and stored safely for disposal away form children.

# Products

## General

### Design point to be at mid point of scale or range.

### Ranges: dual imperial and metric.

## Direct Reading Thermometers

### Industrial, variable angle type, liquid filled, accuracy ± l scale division, 225 mm scale length: to CAN/CGSB14.4 or ASME B40.200.

## Remote Reading Thermometers

### 100 mm diameter liquid filled or vapor activated dial type: to CAN/CGSB-14.4 or ASME B40.200, accuracy within one scale division, brass movement, stainless steel capillary, stainless steel spiral armour, stainless steel bulb and polished brass or stainless steel case for wall mounting.

## Thermometer Wells

### Copper pipe: copper or bronze.

### Steel pipe: brass or stainless steel.

## Pressure Gauges

### Dial type: 112 mm to ASME B40.100, Grade 2A, stainless steel or phosphor bronze bourdon tube having 0.5% accuracy full scale, 1% accuracy for liquid filled.

### Provide:

#### Siphon for steam service.

#### Snubber for pulsating operation.

#### Diaphragm assembly for corrosive service.

#### Gasketted pressure relief back with solid front.

#### Bronze ball valve to Section 23 05 23.01 – Valves – Bronze.

#### Oil filled for high vibration applications, such as pumps.

# Execution

## General

### Install so they can be easily read from floor or platform. If this cannot be accomplished, install remote reading units.

### Install between equipment and first fitting or valve.

## Thermometers

### Install in wells on piping. Provide heat conductive material inside well.

### Install on inlet and outlet of:

#### Heat exchangers.

#### Heating and cooling coils.

#### Boilers.

#### Chillers.

#### Cooling towers, closed circuit coolers and evaporative condensers.

#### DHW tanks.

#### In other locations as indicated.

### Install wells.

### Use extensions where thermometers are installed through insulation.

## Pressure Gauges

### Install in following locations:

#### Suction and discharge of pumps. (Liquid filled.)

#### Upstream and downstream of PRV's.

#### Upstream and downstream of control valves.

#### Inlet and outlet of coils.

#### Inlet and outlet of heat exchangers.

#### Outlet of boilers.

#### In other locations as indicated.

### Install ball valves.

### Use extensions where pressure gauges are installed through insulation.

## Nameplates

### Install engraved lamicoid nameplates as specified in Section 23 05 53.01 - Mechanical Identification, identifying medium.

END OF SECTION