# General

## Summary

### Section Includes:

#### Bronze – valves.

## Related Sections

### Section 01 33 00 – Submittal Procedures

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

## References

### American National Standards Institute (ANSI)/American Society of Mechanical Engineers (ASME)

#### ANSI/ASME B1.20.1, Pipe Threads, General Purpose (Inch.)

#### ANSI/ASME B16.18, Cast Copper Alloy Solder Joint Pressure Fittings

#### ANSI/ASME B16.22, Wrought Copper and Copper Alloy Solder Joint Pressure Fittings.

### American Society for Testing and Materials (ASTM)

#### ASTM A 276, Specification for Stainless Steel Bars and Shapes.

#### ASTM A536, Specification for Ductile Iron Castings.

#### ASTM B 16, Specification for Free-Cutting Brass Rod Bar and Shapes for Use in Screw Machines.

#### ASTM B 62, Specification for Composition Bronze or Ounce Metal Castings.

#### ASTM B 283, Specification for Copper and Copper Alloy Die Forgings (Hot Pressed)

#### ASTM B 505/B505M, Specification for Copper-Base Alloy Continuous Castings.

#### ASTM B584, Specification for Copper Alloy Sand Castings for General Applications.

### Canadian Standards Association (CSA)

#### CSA B242, Groove and Solder Type Mechanical Pipe Couplings.

### Manufacturers Standardization Society of the Valve and Fittings Industry, Inc. (MSS).

#### MSS SP-25, Standard Marking System for Valves, Fittings, Flanges and Unions.

#### MSS SP-80, Bronze Gate, Globe, Angle and Check Valves.

#### MSS SP-110, Ball Valves, Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends.

## Submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:  submit WHMIS SDS – Safety Data Sheets.

#### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

#### Submit data for valves specified this section.

#### Grooved joint couplings and fittings to be indicated on product submittals and to be specifically identified with the applicable style or series designation.

### Closeout Submittals

#### Submit maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## Quality Assurance

### Health and Safety

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

### All grooved joint couplings, fittings, valves, and specialties to be the products of a single manufacturer. Grooving tools to be of the same manufacturer as the grooved components.

## Delivery, Storage and Disposal

### Waste Management and Disposal

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

## Maintenance

### Extra Materials

#### Furnish following spare parts:

##### Gaskets for flanges:  one for every 10 flanged joints.

##### Grooved couplings: IPS and copper-tube dimensioned, one for every 10 (ten) grooved joints.

# Products

## materials

### Except for specialty valves, to be single manufacturer.

### All products to have Canadian registration numbers (CRN).

### End Connections

#### Connection into adjacent piping/tubing:

##### Steel pipe systems: Screwed ends to ANSI/ASME B1.20.1.

##### Copper tube systems.

###### Solder ends ANSI/ASME B16.18.

###### Grooved ends to copper tube dimensions and CSA B242.

###### Push-to-connect ends to ANSI/ASME B16.22 and manufacturer’s standards.

### Lockshield Keys

#### Where lockshield valves are specified, provide 10 keys of each size: malleable iron cadmium plated.

## Gate Valves

### Requirements common to all gate valves, unless specified otherwise:

#### Standard specification: MSS SP-80.

#### Bonnet: with hex. shoulders.

#### Connections: with hex. shoulders.

#### Inspection and pressure testing: to MSS SP-80. Tests to be hydrostatic.

#### Packing: high grade non-asbestos packing.

#### Handwheel: non-ferrous.

#### Handwheel Nut:  bronze to ASTM B62.

#### Class 125, WP=860 kPa steam, 1.4 mPa WOG

#### Class 150 WP=1.03 mPa steam, 2.07 mPa WOG.

### NPS 2 and under, non-rising stem, solid wedge disc, Class 125:

#### Body: with long disc guides, screwed bonnet with stem retaining nut.

#### Operator: Handwheel

### NPS 2 and under, non-rising stem, solid wedge disc, Class 150:

#### Body: with long disc guides, screwed bonnet with stem retaining nut.

#### Operator: Handwheel

### NPS 2 and under, rising stem, split wedge disc, Class 125:

#### Body: with long disc guides, screwed bonnet.

#### Disc: split wedge, bronze to ASTM B283, loosely secured to stem.

#### Operator: Handwheel

### NPS 2 and under, rising stem, solid wedge disc, Class 125:

#### Body: with long disc guides, screwed bonnet.

#### Operator: Handwheel

### NPS 2 and under, rising stem, solid wedge disc, Class 150:

#### Body: with long disc guides, screwed bonnet.

#### Operator: Handwheel

## Globe Valves

### Requirements common to all globe valves, unless specified otherwise:

#### Standard specification: MSS SP-80.

#### Bonnet: union with hex. shoulders.

#### Connections: screwed with hex. shoulders.

#### Inspection and pressure testing: to MSS SP-80. Tests to be hydrostatic.

#### Packing:  non-asbestos.

#### Handwheel: non-ferrous.

#### Handwheel Nut: bronze to ASTM B62.

#### Class 125, WP=860 kPa steam, 1.4 MPa WOG

#### Class 150 WP=1.03 mPa steam, 2.07 MPa WOG.

### NPS 2 and under, composition disc, Class125:

#### Body and bonnet: screwed bonnet.

#### Disc and seat: renewable rotating PTFE disc regrindable bronze seat, loosely secured to bronze stem to ASTM B505.

#### Operator: Handwheel.

### NPS 2 and under, composition disc, Class 150:

#### Body and bonnet: union bonnet.

#### Disc and seat: renewable rotating PTFE disc in easily removable disc holder, regrindable bronze seat, loosely secured to bronze stem to ASTM B505.

#### Operator: Handwheel

### NPS 2 and under, plug disc, Class 150, screwed ends:

#### Body and bonnet: union bonnet.

#### Disc and seat ring: tapered plug type with disc stem ring of stainless steel to ASTM A276, loosely secured to stem.

#### Operator: Handwheel

### Angle valve, NPS 2 and under, composition disc, Class 150:

#### Body and bonnet: union bonnet.

#### Disc and seat: renewable rotating PTFE disc in slip-on easily removable disc holder having integral guides, regrindable bronze seat, loosely secured to stem.

#### Operator: Handwheel.

## Check Valves

### Requirements common to all check valves, unless specified otherwise:

#### Standard specification: MSS SP-80.

#### Connections: with hex agonal shoulders.

#### Class 125, WP=860 kPa steam, 1.4 MPa WOG

#### Class 150 WP=1.03 mPa steam, 2.07 MPa WOG

#### Class 200 1.4 MPa CWP

### NPS 2 and under, swing type, bronze disc, Class 125:

#### Body: Y-pattern with integral seat at 45°, screw-in cap with hex head.

#### Disc and seat: renewable rotating disc, two-piece hinge disc construction; seat: regrindable.

### NPS 2 and under, swing type, bronze disc, Class 150:

#### Body: Y-pattern with integral seat at 45°, screw-in cap with hex head.

#### Disc and seat: renewable rotating disc, two-piece hinge disc construction; seat: regrindable.

### NPS 2 and under, swing type, composition disc, Class 200:

#### Body: Y-pattern with integral seat at 45°, screw-in cap with hex. head.

#### Disc: renewable rotating disc, of number 6 composition to suit service conditions, bronze two-piece hinge disc construction.

### NPS 2 and under, horizontal lift type, composition disc, Class150:

#### Body: with integral seat, union bonnet ring with hex. shoulders, cap.

#### Disc: renewable PTFE for steam,  #6 composition   rotating disc for water, oil or gas service in disc holder having guides top and bottom, of bronze to ASTM B62.

### NPS 2 and under, vertical lift type, bronze disc, Class 125:

#### Disc: rotating disc having guides top and bottom, disc guides, retaining rings.

### NPS 2 and under, vertical or horizontal, lift type, 1380 kPa CWP.

#### Disc: 301 stainless steel, center guided.

## Silent Check Valves

### NPS 2 and under:

#### Body: cast high tensile bronze to ASTM B62 with integral seat.

#### Pressure rating:  Class 125.

#### Connections: screwed ends to ANSI B1.20.1 and with hex. shoulders.

#### Disc and seat: renewable rotating disc.

#### Stainless steel spring, heavy duty.

#### Seat: regrindable.

## Ball Valves

### NPS 2 and under:

#### Body and cap: cast high tensile bronze to ASTM B16 or ASTM B62.

#### Pressure rating: Class 125, 860 MPa steam.

#### Connections: Screwed ends to ANSI B1.20.1 and with hex. shoulders. Push-to-connect, Pressfit ends.

#### Stem: tamperproof ball drive.

#### Stem packing nut: external to body.

#### Ball and seat: replaceable stainless steel or hard chrome, plated brass solid ball and teflon seats.

#### Stem seal: TFE, EPDM, Nitrile, Fluoroelastomer with with external packing nut.

#### Operator: removable lever handle with extension for insulated pipe.

#### Cap and drain for drain service.

## Butterfly Valves

### NPS 2-1/2 through NPS 6.

#### Body: cast bronze per CDA-836 (85-5-5-5).

#### Pressure rating: 2065-kPa CWP.

#### Connections: copper tube dimensioned grooved ends.

#### Disc: ductile iron per ASTM A536 with elastomer coating.

#### Stem: integrally cast with disc.

#### Stem Nuts: nickel plated 416 stainless steel.

#### Operator: gear operator, NPS and over.

# Execution

## Installation

### Install rising stem valves in upright position with stem above horizontal.

### Remove internal parts before soldering.

### Adjoining tube, couplings, and fittings with grooved joint valves shall be copper-tube dimensioned. Flaring tube or fitting ends to accommodate IPS sized valves is not permitted.

### Install valves with unions at each piece of equipment arranged to allow servicing, maintenance, and equipment removal.

#### Unions are not required in installations using grooved mechanical couplings. The couplings shall serve as unions.

## Commissioning

### As part of commissioning activities, develop schedule of valves and record thereon identifier, location, service, purchase order number and date, manufacturer, identification data specified above.

END OF SECTION