# General

## Section Includes

### Valves Cast Steel, gate, globe, and check.

## Related Sections

### Section 01 33 00 – Submittal Procedures

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

## References

### American National Standards Institute (ANSI)/American Society of Mechanical Engineers (ASME)

#### ANSI/ASME B16.5, Pipe Flanges and Flanged Fittings: NPS   through NPS 24 Metric/Inch Standard.

#### ANSI/ASME B16.10, Face-to-Face and End-to-End Dimensions Valves.

#### ANSI/ASME B16.25, Buttwelding Ends.

#### ANSI/ASME B16.34, Valves-Flanged, Threaded, and Welding End.

### American Petroleum Institute (API)

#### API 598, Valve Inspection and Testing

### American Society for Testing and Materials International (ASTM)

#### ASTM A49, Standard Specification for Heat-Treated Carbon Steel Joint Bars, Micro Alloyed Joint Bars, and Forged Carbon Steel Comprise Joint Bars.

#### ASTM A193/A193M, Standard Specification for Alloy-Steel and Stainless Steel Bolting Materials for High-Temperature or High Pressure Service and Other Special Purpose Applications.

#### ASTM A 194/A194M, Specification for Carbon and Alloy Steel Nuts for Bolts for High-Pressure and High-Temperature Service.

#### ASTM A 216/A216M, Specification for Steel Castings, Carbon Suitable for Fusion Welding for High Temperature Service.

#### ASTM B 85, Specification for Aluminum-Alloy Die Castings.

### Manufacturers Standardization Society of the Valve and Fittings Industry, Inc. (MSS).

#### MSS SP-25, Standard Marking System for Valves, Fittings, Flanges and Unions.

#### MSS SP-61, Pressure Testing of Steel Values.

## Submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:  submit WHMIS SDS – Safety Data Sheets in accordance with Section 01 33 00 – Submittal Procedures.

#### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

#### Submit data for valves specified this section.

#### Submit product data in accordance with Section 01 33 00 – Submittal Procedures.

### Closeout Submittals

#### Submit maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## Quality Assurance

### Health and Safety

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## Delivery, Storage and Disposal

### Waste Management and Disposal

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

## Maintenance

### Extra Materials

#### Furnish following spare parts:

#### Valve seats:  one for every 10 valves each size.  Minimum 1.

#### Discs:  one for every 10 valves, each size.  Minimum 1.

#### Stem packing:  one for every 10 valves, each size.  Minimum 1.

#### Valve handles:  2 of each size.

#### Gaskets for flanges:  one for every 10 flanged joints.

# Products

## material

### Except for specialty valves, to be of single manufacturer.

### Valves to be individually tested.

### Requirements common to valves, unless specified otherwise:

#### Pressure-temperature ratings: to ANSI B16.34.

#### Inspections and tests: to API 598.

#### Pressure Testing: to MSS SP-61.

#### Flanged valves:

##### Face-to-face dimensions: to ANSI B16.10.

##### Flange dimensions: to ANSI B16.5 with 1.6 mm raised face

#### Butt-weld valves:

##### End-to-end dimensions: to ANSI B16.10.

##### End dimensions: to ANSI B16.25 bored for standard pipe schedule

#### Hand wheel: non-heating type with raised rim of die-cast aluminum alloy to ASTM B85 or malleable iron to ASTM A49.

#### Markings: to MSS SP-25.

#### Identification:

##### Plate showing catalogue number, size, material of body, disc, stem seat, fluid, pressure-temperature rating.

##### Body markings: manufacturer, size, primary service rating, material symbol.

#### Canadian Registration Number (CRN) required for all products.

## Gate Valves

### NPS 2 1/2 - 12, rising stem, OS&Y, flexible wedge disc, flanged ends, Class150 or 300:

#### Body and multiple-bolted integral yoke and bonnet: cast steel to ASTM A216 WCB, with full length disc guides designed to ensure correct re-assembly.

#### Body/bonnet joint: Flat face male-female with corrugated metallic gasket.

#### Bonnet studs: to ASTM A193/A193M Type B7.

#### Bonnet nuts: to ASTM A194/A194M Type 2H.

#### Stuffing box: including non-galling two-piece ball jointed packing gland, with swing-type eye bolts and nuts.

#### Gland packing: containing corrosion inhibitor to prevent stem pitting.

#### Yoke sleeve: Ni-Resist, minimum melting point above 954°C.

#### Hydraulic grease fitting: for lubrication of yoke sleeve bearing surfaces.

#### Disc: with disc stem ring to connect to stem, guided throughout its travel.

##### NPS 2 1/2 - 6: Solid corrosion and heat resistant 13% chromium steel with minimum hardness of 350 HB.

##### NPS 8 and larger: Carbon steel faced with corrosion and heat resistant 13% chromium steel with minimum hardness of 350 HB.

#### Seat ring: seamless carbon steel with hard-faced cobalt-chromium-tungsten alloy seating surface, slipped in, seal welded, ground to match disc.

#### Stem: heat treated corrosion and heat resistant 13% chromium steel with accurately-cut precision-machined Acme or 60 V threads, top screwed for handwheel nut, T-head disc-stem connection.

#### Operator: see elsewhere this section.

## Globe Valves

### NPS 2 1/2 - 12, rising stem, OS&Y, flanged butt-weld ends, Class150 or 300:

#### Body and multiple-bolted integral yoke and bonnet: cast steel to ASTM A216/A216M WCB.

#### Body/bonnet joint:  Male-female face with corrugated metallic gasket.

#### Bonnet studs: to ASTM A193/A193M Type B7.

#### Bonnet nuts: to ASTM A194/A194M Type 2H.

#### Stuffing box: including non-galling two-piece ball-jointed packing gland, with swing-type eye bolts and nuts.

#### Gland packing: containing corrosion inhibitor to prevent stem pitting.

#### Yoke bushing: Ni-Resist, minimum melting point above 954C.

#### Hydraulic grease fitting: for lubrication of yoke sleeve bearing surfaces.

#### Disc: Plug type with 15 taper seat and bottom guide.

#### Seat rings: with 1.6 mm thick cobalt-chromium-tungsten alloy facings with minimum hardness of 375 HB (cold), slipped in, seal welded, ground to match disc.

#### Stem: heat treated corrosion and heat resistant 13% chromium steel with bonnet bushing, long engagement with yoke bushing for accurate seating, accurately-cut precision-machined Acme or 60 V threads, top screwed for handwheel nut.

#### Operator: see elsewhere this section.

## Valve Operators

### Handwheel: on all gate and globe valves except as specified.

### Handwheel with chain operators: on valves installed more than 2400 mm above floor in Boiler Rooms and Mechanical Equipment Rooms.

## Bypasses for Gate and Globe Valves

### Locations: on valves as indicated.

### Position of bypass valve on main valves: stem vertical or parallel position.

### Size of bypass valve:

#### Main valve up to NPS 8: NPS 3/4.

#### Main valve NPS 10 and over: NPS 1.

### Type of bypass valves:

#### On gate valve: globe, with composition disc, bronze trim, to Section 23 05 23.01 - Valves - Bronze

#### On globe valve: globe, with composition disc, bronze trim, to Section 23 05 23.01 – Valves - Bronze

## Check Valves

### NPS 2 1/2 and over, flanged - ends, Class150 or 300: swing check.

#### Body and multiple-bolted cap: cast steel to ASTM A216/A216M WCB.

#### Cap studs: to ASTM A193/A193M Type B7.

#### Cap nuts: to ASTM A194/A194M Type 2H.

#### Body/cap joint: male-female face with corrugated metallic gasket.

#### Disc: heat treated corrosion and heat resistant 13% chromium steel.

#### Seat rings: heat treated corrosion and heat resistant 13% chromium steel, slipped in, seal welded, ground to match disc.

#### Hinge: ASTM A 216 WCB.

#### Hinge pin: 410 Stainless Steel.

## silent check Valves

### Construction

#### Body:  Cast steel to ASTM with integral seat.

#### Pressure rating:  Class 125, 250.

#### Connections:  Flanged ends.

#### Double bronze disc with SS seat and stem.  Renewable disc, seat, stem and spring, Spring rating must match system design for silent operation and installation.

#### Stainless steel spring, heavy duty.

#### Seat:  regrindable.

# Execution

## Installation

### Install in accordance with manufacturer's recommendations in upright position with stem above horizontal.

## Commissioning

### As part of commissioning activities, develop schedule of valves and record thereon identifier, location, service, purchase order number and date, manufacturer, identification data specified above.

END OF SECTION