# General

## Related Sections

### Section 01 33 00 – Submittal Procedures

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

## References

### American National Standards Institute (ANSI)

##### ANSI B16.5 - Pipe Flanges and Flanged Fittings.

##### ANSI 150 - Flanges and Bolt Dimensions.

##### ANSI B1.20.1 - Unified Screw and Pipe Threads.

### Canadian Standard Association (CSA)

##### CSA B137.6 - CPVC Pipe, Tubing and Fittings for Both Hot and Cold Water Distribution Systems.

### National Sanitation Foundation (NSF)

##### NSF61 - Potable Water Listing.

### Underwriters Listing of Canada (ULC)

##### CAN/ULC S102.2 - Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings and Miscellaneous Materials and Assemblies.

### American Society for Testing and Materials International, (ASTM).

#### ASTM D1784 - Standard Specification for Rigid Poly (Vinyl Chloride) PVC Compounds and Chlorinated Poly (Vinyl Chloride) CPVC compounds.

#### ASTM F439 - Standard Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 80.

#### ASTM F437 - Standard Specification for Threaded Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 80

#### ASTM F1498 - Standard Specification for Taper Pipe Threads 60° for Thermoplastic Pipe and Fittings

### Department of Justice Canada (Jus).

#### Canadian Environmental Protection Act (CEPA).

### National Research Council (NRC)/Institute for Research in Construction.

#### NRCC, National Plumbing Code of Canada (NPC).

## Submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:  submit WHMIS SDS –Safety Data Sheets in accordance with Section 01 33 00 – Submittal Procedures.

#### Submit shop drawings and product data in accordance with Section 01 33 00 – Submittal Procedures.

#### Submit data for valves specified this section.

#### Submit product data in accordance with Section 01 33 00 – Submittal Procedures.

### Closeout Submittals

#### Submit maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## Quality Assurance

### Health and Safety

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

#### All pipe, fittings, and valves to be the products of a single manufacturer.

## Delivery, Storage and Disposal

### Waste Management and Disposal

#### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

## Maintenance

### Extra Materials

#### Gaskets for flanges:  one for every 10 flanged joints.

# Products

## BALL VALVES

### Except for specialty valves, to be of single manufacturer.

### Material

#### The valve body, ball and union shall be made of CPVC compound which shall meet or exceed the requirements of cell classification 23447 according to ASTM D1784

#### Valve seats shall be made of PTFE.

#### O-ring seals shall be made of EPDM or FPM.

### Connections

#### Socket style IPS end connectors shall conform to dimensional standard ASTM F439.

#### Threaded style female NPT connectors shall conform to the dimensional standards ASTM F437, ASTM F1498, and ANSI B1.20.1.

#### Flange style ANSI 150 connectors shall conform to the dimensional standard ANSI B16.5.

### Design Features

#### Valves shall be double blocked with union ends.

#### All sizes shall be full port, and allow for bi-directional flow.

#### Valve handles shall incorporate a tool for adjustment of threaded carrier, and shall be reversible to allow for operation in tight quarters.

### Pressure Tested

#### Valves shall have been pressure tested in both open and closed positions by the manufacturer.

### Pressure and Temperature Rating

#### Valve shall have an operational rating of 1,600kPa at 23o C and 717kPa at 60o C.

### Markings

#### All valves shall be marked to indicate size, valve body and o-ring seal material designation, and manufacturer’s name or trade mark.

#### All valves shall have markings indicating NSF-61 compliance.

#### All valves shall be color coded blue.

# Execution

## Installation

### Install in accordance with manufacturer's recommendations.

## Commissioning

### As part of commissioning activities, develop schedule of valves and record thereon identifier, location, service, purchase order number and date, manufacturer, identification data specified above.

END OF SECTION