# General

## Summary

### Section includes:

#### Concrete housekeeping pads, hangers and supports for mechanical piping, ducting and equipment.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 03 30 00 - Cast-in-Place Concrete.

### Section 05 12 23 - Structural Steel for Buildings.

### Section 05 50 00 - Metal Fabrications.

## References

### American National Standards Institute/ American Society of Mechanical Engineers (ANSI/ASME)

#### ANSI/ASME B31.1, Power Piping, (SI Edition).

### American Society for Testing and Materials (ASTM)

#### ASTM A125, Specification for Steel Springs, Helical, Heat-Treated.

#### ASTM A307, Specification for Carbon Steel Bolts and Studs, 60,000 PSI Tensile Strength.

#### ASTM A563, Specification for Carbon and Alloy Steel Nuts.

### Factory Mutual (FM)

### Health Canada / Workplace Hazardous Materials Information System (WHMIS).

#### Safety Data Sheets (SDS).

### Manufacturer's Standardization Society of the Valves and Fittings Industry (MSS)

#### MSS SP-58, Pipe Hangers and Supports - Materials, Design and Manufacture.

#### ANSI/MSS SP-69, Pipe Hangers and Supports - Selection and Application.

#### MSS SP-89, Pipe Hangers and Supports - Fabrication and Installation Practices.

### Underwriter's Laboratories of Canada (ULC)

## system description

### Design Requirements

#### Construct pipe hanger and support to manufacturer's recommendations utilizing manufacturer's regular production components, parts and assemblies.

#### Base maximum load ratings on allowable stresses prescribed by MSS SP58 or ASME B31.1.

#### Ensure that supports, guides, anchors do not transmit excessive quantities of heat to building structure.

#### Design hangers and supports to support systems under all conditions of operation, allow free expansion and contraction, prevent excessive stresses from being introduced into pipework or connected equipment.

#### Provide for vertical adjustments after erection and during commissioning. Amount of adjustment to be in accordance with MSS SP58.

### Performance Requirements

#### Design supports, platforms, catwalks, hangers, to withstand seismic events for location as per the National Building Code

## SUBMITTALS

### Submittals: in accordance with Section 01 33 00 - Submittal Procedures.

### Shop drawings: submit drawings stamped and signed for approval by Owner.

### Submit shop drawings and product data for following items:

#### Bases, hangers and supports.

#### Connections to equipment and structure.

#### Structural assemblies.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

##### Owner will make available one (1) copy of systems supplier's installation instructions.

### Closeout Submittals:

#### Provide maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals

## QUALITY ASSURANCE

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## General

### Fabricate hangers, supports and sway braces in accordance with ANSI B31.1 and MSS SP-58 and SP-89.

### Use components for intended design purpose only. Do not use for rigging or erection purposes.

## Pipe Hangers

### Finishes:

#### Pipe hangers and supports: galvanized painted with zinc-rich paint after manufacture.

#### Use electro-plating galvanizing process or hot dipped galvanizing process.

#### Ensure steel hangers in contact with copper piping are copper plated or epoxy coated.

### Upper attachment structural: Suspension from lower flange of I-Beam.

#### Cold piping NPS 2 maximum: malleable iron C-clamp with hardened steel cup point setscrew, locknut and carbon steel retaining clip.

##### Rod: 9 mm UL listed, 13 mm FM approved.

#### Cold piping NPS 2 1/2 or greater, hot piping: Malleable iron beam clamp, eye rod, jaws and extension with carbon steel retaining clip, tie rod, nuts and washers, UL listed, FM approved where required to MSS-SP58 and MSS-SP69.

### Upper attachment structural: Suspension from upper flange of I-Beam.

#### Cold piping NPS 2 maximum: Ductile iron top-of-beam C-clamp with hardened steel cup point setscrew, locknut and carbon steel retaining clip, UL listed FM approved where required to MSS SP69.

#### Cold piping NPS 2 1/2 or greater, all hot piping: Malleable iron top-of-beam jaw-clamp with hooked rod, spring washer, plain washer and nut UL listed, FM approved where required.

### Upper attachment to concrete.

#### Ceiling: Carbon steel welded eye rod, clevis plate, clevis pin and cotters with weldless forged steel eye nut. Ensure eye 6 mm minimum greater than rod diameter.

#### Concrete inserts: wedge shaped body with knockout protector plate UL listed FM approved where required to MSS SP-69.

### Shop and field-fabricated assemblies.

#### Trapeze hanger assemblies: MSS SP-89.

#### Steel brackets: MSS SP-89.

#### Sway braces for seismic restraint systems: to MSS SP-89.

### Hanger rods: threaded rod material to MSS SP-58.

#### Ensure that hanger rods are subject to tensile loading only.

#### Provide linkages where lateral or axial movement of pipework is anticipated.

#### Do not use 22 mm or 28 mm rod.

### Pipe attachments: material to MSS SP-58.

#### Attachments for steel piping: carbon steel galvanized.

#### Attachments for copper piping: copper plated black steel.

#### Use insulation saddles for hot pipework.

#### Oversize pipe hangers and supports for insulated pipes.

### Adjustable clevis: material to MSS SP-69, UL listed FM approved, where required clevis bolt with nipple spacer and vertical adjustment nuts above and below clevis.

#### Ensure "U" has hole in bottom for rivetting to insulation shields.

### Yoke style pipe roll: carbon steel yoke, rod and nuts with cast iron roll, to MSS SP-69.

### U-bolts: carbon steel to MSS SP-69 with 2 nuts at each end to ASTM A563.

#### Finishes for steel pipework:  galvanized.

#### Finishes for copper, glass, brass or aluminum pipework: black with formed portion plastic coated or epoxy coated.

### Pipe rollers: cast iron roll and roll stand with carbon steel rod to MSS SP-69.

## Riser Clamps

### Steel or cast iron pipe: galvanized black carbon steel to MSS SP-58, type 42, UL listed FM approved where required.

### Copper pipe: carbon steel copper plated to MSS SP-58, type 42.

### Bolts: to ASTM A307.

### Nuts: to ASTM A563.

## Insulation Protection Shields

### Insulated cold piping:

#### 64 kg/m3 density insulation plus insulation protection shield to: MSS SP-69, galvanized sheet carbon steel. Length designed for maximum 3.0 m span.

### Insulated hot piping:

#### Curved plate 300 mm long, with edges turned up, welded-in centre plate for pipe sizes NPS 12 and over, carbon steel to comply with MSS SP-69.

## Constant Support Spring Hangers

### Springs: alloy steel to ASTM A125, shot peened, magnetic particle inspected, with +/-5% spring rate tolerance, tested for free height, spring rate, loaded height and provided with Certified Mill Test Report(CMTR).

### Load adjustability: 10 % minimum adjustability each side of calibrated load. Adjustment without special tools. Adjustments not to affect travel capabilities.

### Provide upper and lower factory set travel stops.

### Provide load adjustment scale for field adjustments.

### Total travel to be actual travel + 20%. Difference between total travel and actual travel 25 mm minimum.

### Individually calibrated scales on each side of support calibrated prior to shipment, complete with calibration record.

## Variable Support Spring Hangers

### Vertical movement: 13 mm minimum, 50 mm maximum, use single spring pre-compressed variable spring hangers.

### Vertical movement greater than 50 mm: use double spring pre-compressed variable spring hanger with 2 springs in series in single casing.

### Variable spring hanger to be complete with factory calibrated travel stops. Provide certificate of calibration for each hanger.

### Steel alloy springs: to ASTM A125, shot peened, magnetic particle inspected, with +/-5 % spring rate tolerance, tested for free height, spring rate, loaded height and provided with CMTR.

## Equipment Supports

### Fabricate equipment supports not provided by equipment manufacturer from structural grade steel meeting requirements of Section 05 12 23 - Structural Steel for Buildings. Submit calculations with shop drawings.

## Equipment Anchor Bolts and Templates

### Provide templates to ensure accurate location of anchor bolts.

## Platforms and Catwalks

### To Section 05 50 00 - Metal Fabrication.

## House-keeping Pads

### For base-mounted equipment: Concrete, at least 100 mm high, 50 mm larger all around than equipment, and with chamfered edges.

### Concrete: to Section 03 30 00 - Cast-in-place Concrete by Division 3.

## Other Equipment Supports

### From structural grade steel meeting requirements of Section 05 12 23 - Structural Steel for Buildings.

### Submit structural calculations with shop drawings.

# Execution

## manufacturer’s instructions

### Compliance:  comply with manufacturer’s written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with:

#### Manufacturer's instructions and recommendations.

### Vibration Control Devices:

#### Install on piping systems at pumps, boilers, chillers, cooling towers, elsewhere as indicated.

### Clamps on riser piping:

#### Support independent of connected horizontal pipework using riser clamps and riser clamp lugs welded to riser.

#### Bolt-tightening torques to be to industry standards.

#### Steel pipes: Install below coupling or shear lugs welded to pipe.

#### Cast iron pipes: Install below joint.

### Clevis plates:

#### Attach to concrete with 4 minimum concrete inserts, one at each corner.

### Provide supplementary structural steelwork where structural bearings do not exist or where concrete inserts are not in correct locations.

### Use approved constant support type hangers where:

#### vertical movement of pipework is 13 mm or more,

#### transfer of load to adjacent hangers or connected equipment is not permitted.

### Use variable support spring hangers where:

#### transfer of load to adjacent piping or to connected equipment is not critical.

#### variation in supporting effect does not exceed 25 % of total load.

## Hanger Spacing

### Plumbing piping: most stringent requirements of Canadian Plumbing Code

### Fire protection: to applicable fire code.

### Gas and fuel oil piping: up to NPS 1/2: every 1.8 m.

### Copper piping: up to NPS 1/2: every 1.5 m.

### Hydronic, steam, condensate, rigid, and flexible joint roll groove pipe: in accordance with table below, but not less than one hanger at joints.

| Maximum Pipe Size: NPS | Maximum Spacing: Steel | Maximum Spacing: Copper |
| --- | --- | --- |
| up to 1-1/4 | 2.1 m | 1.8 m |
| 1-1/2 | 2.7 m | 2.4 m |
| 2 | 3.0 m | 2.7 m |
| 2-1/2 | 3.6 m | 3.0 m |
| 3 | 3.6 m | 3.0 m |
| 3-1/2 | 3.9 m | 3.3 m |
| 4 | 4.2 m | 3.6 m |
| 5 | 4.8 m |  |
| 6 | 5.1 m |  |
| 8 | 5.7 m |  |
| 10 | 6.6 m |  |
| 12 | 6.9 m |  |

### Within 300 mm of each elbow.

### Pipework greater than NPS 12: to MSS SP69.

## Hanger Installation

### Install hanger so that rod is vertical under operating conditions.

### Adjust hangers to equalize load.

### Support from structural members. Where structural bearing does not exist or inserts are not in suitable locations, provide supplementary structural steel members, comprised of angel iron or c-channel.

## Horizontal Movement

### Angularity of rod hanger resulting from horizontal movement of pipework from cold to hot position not to exceed 4 degrees from vertical.

### Where horizontal pipe movement is less than 13 mm, offset pipe hanger and support so that rod hanger is vertical in the hot position.

## Final Adjustment

### Adjust hangers and supports:

#### Ensure that rod is vertical under operating conditions.

#### Equalize loads.

### Adjustable clevis:

#### Tighten hanger load nut securely to ensure proper hanger performance.

#### Tighten upper nut after adjustment.

### C-clamps:

#### Follow manufacturer's recommended written instructions and torque values when tightening C-clamps to bottom flange of beam.

### Beam clamps:

#### Hammer jaw firmly against underside of beam.

END OF SECTION