# General

## summary

### Section Includes:

#### Materials and requirements for the identification of piping systems, duct work, valves and controllers, including the installation and location of identification systems.

#### Sustainable requirements for construction and verification.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 09 91 23 - Interior Painting.

## References

### Canadian Gas Association (CGA)

#### CSA/CGA B149.1, Natural Gas and Propane Installation Code.

#### CSAZ7396.1 Medical Gas pipeline Systems – Part 1: Pipelines for medical gases and vacuum.

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-24.3, Identification of Piping Systems.

### National Fire Protection Association (NFPA)

#### NFPA 13, Standard for the Installation of Sprinkler Systems.

#### NFPA 14, Standard for the Standpipe and Hose Systems.

## submittals

### Product Data:

#### Submittals:  in accordance with Section 01 33 00 - Submittal Procedures.

#### Product data to include paint colour chips, other products specified in this section.

#### Samples:

##### Submit samples in accordance with Section 01 33 00 – Submittal Procedures.

##### Samples to include nameplates, labels, tags, lists of proposed legends.

## Quality assurance

### Quality assurance submittals:  submit following in accordance with Section 01 33 00 – Submittal Procedures.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 – Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer’s written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Dispose of unused paint coating material at official hazardous material collections site approved by Owner.

#### Do not dispose of unused paint coating material into sewer system, into streams, lakes, onto ground or in locations where it will pose health or environmental hazard.

# Products

## Manufacturer's Equipment Nameplates

### Metal or plastic laminate nameplate mechanically fastened to each piece of equipment by manufacturer.

### Lettering and numbers to be raised or recessed.

### Information to include, as appropriate:

#### Equipment: Manufacturer's name, model, size, serial number, capacity.

#### Motor: voltage, Hz, phase, power factor, duty, frame size.

## System Nameplates

### Colours:

#### Hazardous: red letters, white background.

#### Elsewhere: black letters, white background (except where required otherwise by applicable codes).

### Construction:

#### 3 mm thick laminated plastic or white anodized aluminum, matte finish, with square corners, letters accurately aligned and machine engraved into core.

### Sizes:

#### Conform to following table:

| Size # mm | Sizes (mm) | No. of Lines | Height of Letters (mm) |
| --- | --- | --- | --- |
| 1 | 10 x 50 | 1 | 3 |
| 2 | 13 x 75 | 1 | 5 |
| 3 | 13 x 75 | 2 | 3 |
| 4 | 20 x 100 | 1 | 8 |
| 5 | 20 x 100 | 2 | 5 |
| 6 | 20 x 200 | 1 | 8 |
| 7 | 25 x 125 | 1 | 12 |
| 8 | 25 x 125 | 2 | 8 |
| 9 | 35 x 200 | 1 | 20 |

#### Use maximum of 25 letters/numbers per line.

### Locations:

#### Terminal cabinets, control panels: Use size # 5.

#### Equipment in Mechanical Rooms: Use size # 9.

## Existing Identification Systems

### Apply existing identification system to new work.

### Where existing identification system does not cover for new work, use identification system specified this section.

### Before starting work, obtain written approval of identification system from Owner.

## Piping Systems Governed by Codes

### Identification:

#### Natural gas:  to CSA/CGA B149.1, authority having jurisdiction.

#### Propane gas: to CSA/CGA B149.1 authority having jurisdiction.

#### Sprinklers: to NFPA 13.

#### Standpipe and hose systems: to NFPA 14.

#### Medical Gas:  to CAN/CSA Z7396.1.

## Identification of Piping Systems

### Identify contents by background colour marking, pictogram (as necessary), legend; direction of flow by arrows. To CAN/CGSB 24.3 except where specified otherwise.

### Pictograms:

#### Where required, to Workplace Hazardous Materials Information System (WHMIS) regulations.

### Legend:

#### Block capitals to sizes and colours listed in CAN/CGSB 24.3.

### Arrows showing direction of flow:

#### Outside diameter of pipe or insulation less than 75 mm: 100 mm long x 50 mm high.

#### Outside diameter of pipe or insulation 75 mm and greater: 150 mm long x 50 mm high.

#### Use double-headed arrows where flow is reversible.

### Extent of background colour marking:

#### To full circumference of pipe or insulation.

#### Length to accommodate pictogram, full length of legend and arrows.

### Materials for background colour marking, legend, arrows:

#### Pipes and tubing 20 mm and smaller: Waterproof and heat-resistant pressure sensitive plastic marker tags.

#### All other pipes: Pressure sensitive plastic-coated cloth or vinyl with protective overcoating, waterproof contact adhesive undercoating, suitable for ambient of 100%RH and continuous operating temperature of 150oC and intermittent temperature of 200oC.

### Colours and Legends:

#### Where not listed, obtain direction from Owner.

#### Colours for legends, arrows, to following table:

| Background colour | Legend, arrows |
| --- | --- |
| Yellow | BLACK |
| Green | WHITE |
| Red | WHITE |

#### Background colour marking and legends for piping systems:

| Contents | Background colour marking | Legend |
| --- | --- | --- |
| ** Add design temperature |
| ++ Add design temperature and pressure |
| Raw water | Green | RAW WATER |
| River water | Green | RIVER WATER |
| Sea water | Green | SEA WATER |
| City water | Green | CITY WATER |
| Treated water | Green | TREATED WATER |
| Brine | Green | BRINE |
| Condenser water supply | Green | COND. WTR. SUPPLY |
| Condenser water return | Green | COND. WTR. RETURN |
| Chilled water supply | Green | CH. WTR. SUPPLY |
| Chilled water return | Green | CH. WTR. RETURN |
| Hot water heating supply | Yellow | HEATING SUPPLY |
| Hot water heating return | Yellow | HEATING RETURN |
| High temp HW Htg. supply | Yellow | HTHW HTG. SUPPLY++ |
| High temp HW Htg. return | Yellow | HTHW HTG. RETURN++ |
| Make-up water | Yellow | MAKE-UP WTR |
| Boiler feed water | Yellow | BLR. FEED WTR |
| Steam ___kPa | Yellow | ___kPa STEAM |
| Steam condensate (gravity) | Yellow | ST.COND.RET (GRAVITY) |
| Steam condensate (pumped) | Yellow | ST.COND.RET (PUMPED) |
| Safety valve vent | Yellow | STEAM VENT |
| Intermittent blow-off | Yellow | INT. BLOW-OFF |
| Continuous blow-off | Yellow | CONT. BLOW-OFF |
| Chilled drinking water | Green | CH. DRINK WTR |
| Drinking water return | Green | CH. DRINK WTR. CIRC |
| Domestic hot water supply | Green | DOM. HW SUPPLY |
| Dom. HWS recirculation | Green | DOM. HW CIRC |
| Domestic cold water supply | Green | DOM. CWS |
| Waste water | Green | WASTE WATER |
| Contaminated lab waste | Yellow | CONT. LAB WASTE |
| Acid waste | Yellow | ACID WASTE (add source) |
| Storm water | Green | STORM |
| Sanitary | Green | SAN |
| Plumbing vent | Green | SAN. VENT |
| Refrigeration suction | Yellow | REF. SUCTION |
| Refrigeration liquid | Yellow | REF. LIQUID |
| Refrigeration hot gas | Yellow | REF. HOT GAS |
| No. ___ fuel oil suction | Yellow | # ___ FUEL OIL |
| No. ___ fuel oil return | Yellow | # ___ FUEL OIL |
| Engine exhaust | Yellow | ENGINE EXHAUST |
| Lubricating oil | Yellow | LUB. OIL |
| Hydraulic oil | Yellow | HYDRAULIC OIL |
| Gasoline | Yellow | GASOLINE |
| Natural gas | to Codes |  |
| Propane | to Codes |  |
| Gas regulator vents | to Codes |  |
| Distilled water | Green | DISTILL. WTR |
| Demineralized water | Green | DEMIN. WATER |
| Chlorine | Yellow | CHLORINE |
| Nitrogen | Yellow | NITROGEN |
| Oxygen | Yellow | OXYGEN |
| Compressed air (<700kPa) | Green | COMP. AIR ___ kPa |
| Compressed air (>700kPa) | Yellow | COMP. AIR ___ kPa |
| Vacuum | Green | VACUUM |
| Fire protection water | Red | FIRE PROT. WTR |
| Sprinklers | Red | SPRINKLERS |
| Carbon dioxide | Red | CO2 |
| Instrument air | Green | INSTRUMENT AIR |
| Control air tubing | To Section 25 05 54 – EMCS: Identification |
| Conduit for low voltage control wiring | To Section 25 05 54 – EMCS: Identification |
| Medical Gases | To Code |

## Identification DUCTWORK systems

### 50 mm high stencilled letters and directional arrows 150 mm long x 50 mm high.

### Colours: Black, or co-ordinated with base colour to ensure strong contrast.

### Identify system: e.g. Supply AHU-1, Exhaust F-7.

## Valves, Controllers

### Brass tags 12 mm diameter with stamped identification data filled with black paint.

### Include flow diagrams for each system, of approved size, showing charts and schedules with identification of each tagged item, valve type, service, function, normal position, location of tagged item.

## Controls Components Identification

### Identify all systems, equipment, components, controls, sensors with system nameplates specified in section 25 05 54 – EMCS:  Identification.  If no EMCS included in project, identification as per this section.

### Inscriptions to include function and (where appropriate) fail-safe position, component ID name.

## Language

### Identification to be in English.

# Execution

## manufacturer’s instructions

### Compliance:  comply with manufacturer’s written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Timing

### Provide identification only after all painting specified in Section 09 91 23 - Interior Painting has been completed.

## Installation

### Perform work in accordance with CAN/CGSB-24.3 except as specified otherwise.

### Provide ULC and/or CSA registration plates as required by respective agency.

## Nameplates

### Locations:

#### In conspicuous location to facilitate easy reading and identification from operating floor.

### Standoffs:

#### Provide for nameplates on hot and/or insulated surfaces.

### Protection

#### Do not paint, insulate or cover in any way.

## Location of Identification on Piping and Ductwork Systems

### On long straight runs in open areas in boiler rooms, equipment rooms, galleries, tunnels: At not more than 17 m intervals and more frequently if required to ensure that at least one is visible from any one viewpoint in operating areas and walking aisles.

### Adjacent to each change in direction.

### At least once in each small room through which piping or ductwork passes.

### On both sides of visual obstruction or where run is difficult to follow.

### On both sides of separations such as walls, floors, partitions.

### Where system is installed in pipe chases, ceiling spaces, galleries, confined spaces, at entry and exit points, and at access openings.

### At beginning and end points of each run and at each piece of equipment in run.

### At point immediately upstream of major manually operated or automatically controlled valves, dampers, etc. Where this is not possible, place identification as close as possible, preferably on upstream side.

### Identification to be easily and accurately readable from usual operating areas and from access points.

#### Position of identification to be approximately at right angles to most convenient line of sight, considering operating positions, lighting conditions, risk of physical damage or injury and reduced visibility over time due to dust and dirt.

## Valves, Controllers

### Valves and operating controllers, except at plumbing fixtures, radiation, or where in plain sight of equipment they serve: Secure tags with non-ferrous chains or closed "S"hooks.

### Install one copy of flow diagrams, valve schedules mounted in frame behind non-glare glass where directed by Owner. Provide one copy (reduced in size if required) in each operating and maintenance manual.

### Number valves in each system consecutively.

## Cleaning

### Proceed in accordance with Section 01 74 00 – Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, rubbish, tools and equipment.

END OF SECTION