# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal

### Section 23 05 29 - Hangers and Supports for HVAC Piping and Equipment

### Section 23 05 53.01 – Mechanical Identification.

## REFERENCES

### American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE)

#### ANSI/ASHRAE/IESNA 90.1, SI; Energy Standard for Buildings Except Low-Rise Residential Buildings.

### American Society for Testing and Materials International, (ASTM)

#### ASTM B209M, Specification for Aluminum and Aluminum Alloy Sheet and Plate (Metric).

#### ASTM C335, Test Method for Steady State Heat Transfer Properties of Horizontal Pipe Insulation.

#### ASTM C411, Test Method for Hot-Surface Performance of High-Temperature Thermal Insulation.

#### ASTM C449/C449M, Standard Specification for Mineral Fiber-Hydraulic-Setting Thermal Insulating and Finishing Cement.

#### ASTM C547, Specification for Mineral Fiber Pipe Insulation.

#### ASTM C553, Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications.

#### ASTM C612, Specification for Mineral Fiber Block and Board Thermal Insulation.

#### ASTM C795, Specification for Thermal Insulation for Use with Austenitic Stainless Steel.

#### ASTM C921, Standard Practice for Determining Properties of Jacketing Materials for Thermal Insulation.

### Canadian General Standards Board (CGSB)

#### CGSB 51-GP-52Ma, Vapour Barrier, Jacket and Facing Material for Pipe, Duct and Equipment Thermal Insulation.

### Thermal Insulation Association of Canada (TIAC): National Insulation Standards.

### Underwriters Laboratories of Canada (ULC)

#### CAN/ULC-S102, Surface Burning Characteristics of Building Materials and Assemblies.

### National Energy Code of Canada for Buildings (NECB)

## DEFINITIONS

### For purposes of this section:

#### "CONCEALED" - insulated mechanical services and equipment in suspended ceilings and non-accessible chases and furred-in spaces.

#### "EXPOSED" - will mean "not concealed" as defined herein.

#### Insulation systems - insulation material, fasteners, jackets, and other accessories.

### TIAC Codes:

#### CRD: Commercial Round Ductwork,

#### CRF: Commercial Rectangular Finish.

## SHOP DRAWINGS

### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Submit for approval manufacturer's catalogue literature related to installation, fabrication for duct jointing recommendations.

## SAMPLES

### Submit samples in accordance with Section 01 33 00 - Submittal Procedures.

### Submit for approval: complete assembly of each type of insulation system, insulation, coating, and adhesive proposed. Mount sample on 12 mm plywood board. Affix typewritten label beneath sample indicating service.

## MANUFACTURERS' INSTRUCTIONS

### Submit manufacturer's installation instructions in accordance with Section 01 33 00 - Submittal Procedures.

### Installation instructions to include procedures used and installation standards achieved.

## QUALIFICATIONS

### Installer: certified in performing work of this section, and have at least 5 years successful experience in this size and type of project, qualified to standards of TIAC.

## DELIVERY, STORAGE AND HANDLING

### Deliver materials to site in original factory packaging, labelled with manufacturer's name, address.

### Protect from weather and construction traffic.

### Protect against damage from any source.

### Store at temperatures and conditions recommended by manufacturer.

## waste management and disposal

### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction / Demolition Waste Management and Disposal.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal materials from landfill to metal recycling facility approved by Owner.

### Divert unused adhesive material from landfill to official hazardous material collections site approved by Owner.

### Do no dispose of unused adhesive materials into sewer systems, into lakes, streams, onto ground or in other locations where it will pose health or environmental hazard.

# Products

## FIRE AND SMOKE RATING

### In accordance with CAN/ULC-S102:

#### Maximum flame spread rating: 25.

#### Maximum smoke developed rating: 50.

## INSULATION

### Mineral fibre: as specified includes glass fibre, rock wool, slag wool.

### Thermal conductivity ("k" factor) not to exceed specified values at 24oC mean temperature when tested in accordance with ASTM C335.

### TIAC Code C-1: Rigid mineral fibre board to ASTM C612, with factory applied vapour retarder jacket to CGSB 51-GP-52Ma (as scheduled in PART 3 of this Section).

### TIAC Code C-2: Mineral fibre blanket to ASTM C553 faced with factory applied vapour retarder jacket to CGSB 51-GP-52Ma (as scheduled in PART 3 of this section).

#### Mineral fibre: to ASTM C553.

#### Jacket: to CGSB 51-GP-52Ma.

#### Maximum "k" factor: to ASTM C553.

## JACKETS

### Canvas:

#### 220 gm/m2 cotton, plain weave, treated with dilute fire retardant lagging adhesive to ASTM C921.

### Lagging adhesive: Compatible with insulation.

### Aluminum:

#### To ASTM B209 with moisture barrier as scheduled in PART 3 of this section.

#### Thickness: 0.40 mm sheet.

#### Finish: Stucco embossed or corrugated.

#### Jacket banding and mechanical seals: 12 mm wide, 0.5 mm thick stainless steel.

### Stainless steel:

#### Type: 304 or 316 where additional corrosion protection is required.

#### Thickness:  0.25 mm sheet.

#### Finish: Corrugated or stucco embossed.

#### Jacket banding and mechanical seals: 12mm wide, 0.5 mm thick stainless steel.

## ACCESSORIES

### Vapour retarder lap adhesive:

#### Water based, fire retardant type, compatible with insulation.

### Indoor Vapour Retarder Finish:

#### Vinyl emulsion type acrylic, compatible with insulation.

### Insulating Cement: hydraulic setting on mineral wool, to ASTM C449.

### ULC Listed Canvas Jacket:

#### 220 gm/m2 cotton, plain weave, treated with dilute fire retardant lagging a

#### dhesive to ASTM C921.

### Outdoor Vapour Retarder Mastic:

#### Vinyl emulsion type acrylic, compatible with insulation.

#### Reinforcing fabric: Fibrous glass, untreated 305 g/m2.

### Tape: self-adhesive, aluminum, reinforced, 75 mm wide minimum.

### Contact adhesive: quick-setting

### Canvas adhesive: washable.

### Tie wire: 1.5 mm stainless steel.

### Banding: 12 mm wide, 0.5 mm thick stainless steel.

### Facing: 25 mm galvanized steel hexagonal wire mesh stitched on one face of insulation.

### Fasteners:  4 mm diameter pins with 35 mm diameter or square clips, length to suit thickness of insulation.

# Execution

## PRE-INSTALLATION REQUIREMENTS

### Pressure testing of ductwork systems complete, witnessed and certified.

### Surfaces clean, dry, free from foreign material.

## INSTALLATION

### Install in accordance with TIAC National Standards.

### Apply materials in accordance with manufacturer’s instructions and as indicated.

### Use two layers with staggered joints when required nominal thickness exceeds 75 mm.

### Maintain uninterrupted continuity and integrity of vapour retarder jacket and finishes.

#### Hangers, supports to be outside vapour retarder jacket.

### Supports, Hangers in accordance with Section 23 05 29 - Hangers and Supports for HVAC Piping and Equipment

#### Apply high compressive strength insulation where insulation may be compressed by weight of ductwork.

### Fasteners: At 300 mm oc in horizontal and vertical directions, minimum two rows each side.

## DUCTWORK INSULATION SCHEDULE

### Insulation types and thicknesses: Conform to following Table:

|  | TIAC Code | Vapour Retarder | Thickness (mm) |
| --- | --- | --- | --- |
| Rectangular cold and dual temperature supply air ducts (exposed) | C-1 | yes | 50 |
| Round cold and dual temperature supply air ducts (concealed) | C-2 | yes | 50 |
| Rectangular warm air ducts (exposed) | C-1 | no | 25 |
| Round warm air ducts (exposed) | C-1 | no | 25 |
| Rectangular cold and dual temperature supply air ducts (concealed) | C-2 | Yes | 25 |
| Round cold and dual temperature supply air ducts (exposed) | C-1 | yes | 50 |
| Rectangular warm air ducts (concealed) | C-2 | No | 25 |
| Round warm air ducts (concealed) | C-2 | No | 25 |
| Supply, return and exhaust ducts exposed in space being served |  |  | none |
| Outside air ducts to mixing plenum | C-1 | yes | 50 |
| Mixing plenums | C-1 | yes | 25 |
| Exhaust duct between dampers and louvers | C-1 | no | 50 |
| Rectangular ducts outside | C-1 | special | 50 |
| Round ducts outside | C-1 | special | 50 |
| Acoustically lined ducts | See Section 23 33 53- Duct Liners |

### Exposed round ducts 600 mm and larger, smaller sizes where subject to abuse:

#### Use TIAC code C-1 insulation, scored to suit diameter of duct.

### Finishes: Conform to following table:

|  | TIAC Code |
| --- | --- |
|  | Rectangular | Round |
| Indoor, concealed | None | none |
| Indoor, exposed within mechanical room | CRF/1 | CRD/2 |
| Indoor, exposed elsewhere | CRF/2 | CRD/3 |
| Outdoor, exposed to precipitation | CRF/3 | CRD/4 |
| Outdoor, elsewhere | CRF/4 | CRD/5 |

END OF SECTION