# General

## Related Sections

### Section 01 91 13.13 – Commissioning (Cx) Requirements: supplemented as specified herein.

### Section 22 05 15 – Plumbing Specialities and Accessories.

### Section 23 05 93 – Testing, Adjusting and Balancing for HVAC.

### Section 23 08 02 – Cleaning and Start-up of Mechanical Piping Systems.

### Section 23 11 13 – Facility Fuel-Oil Piping.

### Section 22 11 18 – Domestic Water Piping Copper.

### Section 23 21 13.02 – Hydronic Systems: Steel.

### Section 23 23 00 – Copper Tubing and Fittings Refrigerant.

## References

### ASTM E202, Standard Test Methods for Analysis of Ethylene Glycols and Propylene Glycols.

## Cleaning and Start-up of Mechanical Piping Systems

### In accordance with Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems.

## Hydronic Systems - Performance Verification (PV)

### Perform hydronic systems performance verification after cleaning is completed and      system is in full operation.

### When systems are operational, perform following tests:

#### Conduct full scale tests at maximum design flow rates, temperatures and pressures for continuous consecutive period of two (2) working days to demonstrate compliance with design criteria.

#### Verify performance of hydronic system circulating pumps as specified in relevant technical sections, recording system pressures, temperatures, fluctuations by simulating maximum design conditions and varying.

##### Pump operation.

##### Boiler and/or chiller operation.

##### Pressure bypass open/closed.

##### Control pressure failure.

##### Maximum heating demand.

##### Maximum cooling demand.

##### Boiler and/or chiller failure.

##### Cooling tower (and/or industrial fluid cooler) fan failure.

##### Outdoor reset. Re-check heat exchanger output supply temperature at 100% and 50% reset, maximum water temperature.

## Hydronic System Capacity Test

### Timing: After:

#### TAB has been completed

#### Verification of operating, limit, safety controls.

#### Verification of primary and secondary pump flow rates.

#### Verification of accuracy of temperature and pressure sensors and gauges.

### Calculate system capacity at test conditions.

### Using manufacturer's published data and calculated capacity at test conditions, extrapolate system capacity at design conditions.

### When capacity test is completed, return controls and equipment status to normal operating conditions.

### Submit sample of system water to approved testing agency to determine if chemical treatment is correct. Include cost.

### Heating system capacity test:

#### Perform capacity test when ambient temperature is within 10% of design conditions. Simulate design conditions by:

##### Increasing OA flow rates through heating coils (in this case, monitor heating coil discharge temperatures at all times to ensure that coils are not subjected to freezing conditions) or

##### Reducing space temperature by turning off heating system for sufficient period of time before starting testing.

#### Test procedures:

##### Open fully heat exchanger, heating coil and radiation control valves.

##### With boilers on full firing and hot water heating supply temperature stabilized, record flow rates and supply and return temperatures simultaneously.

##### Conduct flue gas analysis test on boilers at full load and at low fire conditions.

### Chilled water system capacity test:

#### Perform capacity test when ambient temperature is within 10% of design conditions. Simulate design conditions by:

##### Adding heat from building heating system or

##### Raising space temperature by turning off cooling and air systems for sufficient period of time before starting testing and pre-heating building to summer design space temperature (occupied) or above. Set OAD and RAD for minimum outside air if OAT is near outside design temperature or to maximum recirculation if RAT is greater that OAT. RAT to be at least 230C.

#### Test procedures:

##### Open fully cooling coil control valves.

##### Set thermostats on associated AHU's for maximum cooling.

##### Set AHU's for design maximum air flow rates.

##### Set load or demand limiters on chillers to 100%

##### After system has stabilized, record chilled water, condenser water, etc., flow rates and supply and return temperatures simultaneously.

## Condenser Water and Humidification Systems

### In addition to procedures specified above, perform following:

#### Add chemicals once or twice per week as required.

#### Perform TAB as specified Section 23 05 93 - Testing, Adjusting and Balancing for HVAC.

#### Set up and adjust drip feeders, timer controls, and pump strokes as required to maintain required chemical feed rates.

#### Inject inhibitor into cooling tower sump.

## STEAM SYSTEMS

### Performance verification:

#### When systems are operational, perform relevant tests of steam and condensate return piping systems as specified under hydronic systems.

#### Verify operation of components of steam system including:

##### Steam traps by:

###### Measuring temperature of condensate return and/or using audio-sensing devices.

###### Use of other approved methods.

##### Flash tanks.

##### Thermostatic vents.

#### Verify performance of condensation units, including:

##### Pump capacity at design temperature.

##### Controls.

#### Verify performance of condensate return system to ensure return of maximum quantity of condensate return water at with minimum temperature drop.

#### Adjust piping system as required to eliminate water hammer.

### Monitor system continuously until acceptance for proper operation components including steam traps, thermostatic vents, flash tanks and condensate pumping units.

## Glycol Systems

### Test to prove concentration will prevent freezing to minus 400C Test inhibitor strength and include in procedural report. Refer to ASTM E202.

## Fuel Oil Systems

### Environmental protection systems:

#### Test oil storage tank leakage detection system using manufacturer's recommended procedures.

#### Test spill protection and over-fill protection systems using manufacturer's recommended procedures.

### Fuel oil pumps:

#### Check strainers on pump inlet, relief valve on pump outlet with discharge to oil return piping, pressure gauge on strainer inlet, pump inlet and pump discharge.

#### Verify pump performance.

#### Pump performance to be within plus 20% and minus 0% of design.

### Operational Tests:

#### Timing: Perform at same time as 100% and 105% boiler PV tests.

#### Charge system and verify operation.

#### Verify adequacy of flow rates and pressure from storage facilities to burners.

#### Verify accurate metering of fuel to burners.

#### For further details refer to relevant sections of mechanical Division.

### Notify authorities having jurisdiction to enable witnessing of tests as required.

## Potable Water Systems

### When cleaning is completed and system filled:

#### Verify performance of equipment and systems as specified elsewhere in mechanical Division.

#### Check for proper operation of water hammer arrestors. Run one outlet for 10 seconds, then shut of water immediately. If water hammer occurs, replace water hammer arrestor. Repeat for each outlet and flush valve.

#### Confirm water quality consistent with supply standards, verifying that no residuals remain as a result of flushing and/or cleaning.

## Wet and Dry Pipe Sprinkler System, Standpipe and Hose Systems

### Cleaning, testing, start-up, performance verification of equipment, systems, components, and devices is specified elsewhere in other mechanical Divisions.

### Verification of controls, detection devices, alarm devices is specified other mechanical and electrical Divisions.

### Demonstrate that fire hose will reach to most remote location regardless of partitions, obstructions, etc.

### Verify operation of interlocks between HVAC systems and fire alarm systems.

## Sanitary and Storm Drainage Systems

### Buried systems: Perform tests prior to back-filling. Perform hydraulic tests to verify grades and freedom from obstructions.

### Ensure that traps are fully and permanently primed.

### Ensure that fixtures are properly anchored, connected to system.

### Operate flush valves, tank and operate each fixture to verify drainage and no leakage.

### Cleanouts: Refer to Section 22 05 15 - Plumbing Specialities and Accessories.

### Roof drains:

#### Refer to Section 22 05 15 - Plumbing Specialities and Accessories.

#### Remove caps as required.

## Reports

### In accordance with Section 01 91 13.13 –Commissioning (Cx) Requirements: supplemented as specified herein.

## Training

#### In accordance with Section 01 91 13.13 –Commissioning (Cx) Requirements: supplemented as specified in relevant specification sections

# Products (Not applicable)

# EXECUTION (Not applicable)

END OF SECTION