# General

summary

### Section Includes:

#### Procedures and cleaning solutions for cleaning mechanical piping systems.

## Related Sections

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 23 05 93 - Testing, Adjusting and Balancing of HVAC

### Section 23 25 00 - HVAC Water Treatment.

References

### American Society for Testing and Materials International (ASTM)

#### ASTM E202 – Standard Test Methods for Analysis of Ethylene Glycols and Propylene Glycols.

### Health Canada / Workplace Hazardous Materials Information System (WHMIS).

#### Safety Data Sheets (SDS).

submittals

### Product Data:

#### Submit manufacturer’s printed product literature, specifications and datasheet in accordance with Section 01 33 00 – Submittal Procedures.  Include product characteristics, performance criteria, and limitations.

#### Quality assurance submittals:  submit following in accordance with Section 01 33 00 – Submittal Procedures.

##### Instructions:  submit manufacturer’s installation instructions.

###### Owner will make available one (1) copy of systems supplier installation instructions.

quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading.

#### Deliver, store and handle in accordance with manufacturer’s written instructions and Section 01 61 00 – Common Product Requirements.

### Waste Management and Disposal:

#### Construction / Demolition Waste Management and Disposal:  separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction / Demolition Waste Management and Disposal.

# Products

Cleaning Solutions

### Low foaming detergent at all temperatures

### No pH neutralization required

### Designed for use on most metals including aluminium

### Bio-degradable

### Phosphate Free

### Nitrite Free

# Execution

Cleaning Hydronic and Steam Systems

### Timing

#### Systems to be operational, hydrostatically tested and with safety devices functional, before cleaning is carried out.

### Cleaning Agency:

#### Retain qualified water treatment specialist to perform system cleaning.

### Install instrumentation such as flow meters, orifice plates, pitot tubes, flow metering valves only after cleaning is certified as complete by water treatment specialist.

### Cleaning procedures:

#### Provide detailed report outlining proposed cleaning procedures at least 4 weeks prior to proposed starting date. Report to include:

##### Cleaning procedures, flow rates, elapsed time.

##### Chemicals and concentrations to be used.

##### Inhibitors and concentrations.

##### Specific requirements for completion of work.

##### Special precautions for protecting piping system materials and components.

##### Complete analysis of water to be used to ensure water will not damage systems or equipment.

### Conditions at time of cleaning of systems

#### Systems to be free from construction debris, dirt and other foreign material.

#### Control valves to be operational, fully open to ensure that terminal units can be cleaned properly.

#### Strainers to be clean prior to initial fill.

#### Install temporary filters on pumps not equipped with permanent filters.

#### Install pressure gauges on strainers to detect plugging.

### Report on Completion of Cleaning

#### When cleaning is completed, submit report, complete with certificate of compliance with specifications of cleaning component supplier.

### Hydronic Systems:

#### Flush system thoroughly with water, back flush pump, strainers, blow down drain valves and risers to remove all loose debris.  Remove accumulated sludge in boilers if necessary.

#### Then add 2% solution of low foaming detergent to the system through a by-pass feeder or another feeding device.

#### Circulate for 36 hours at 82o C.  For chilled systems, circulate at least 48 hours at ambient temperature.

#### During recirculation, back flush strainers, drain valves and risers at their lowest point once every 8 hours.

#### Drain cleaning water completely.

#### Then fill and drain system several times.  Circulate 30 minutes every time the system is refilled.

#### Bleed system at several points until water is clear and non-foaming.  Clean pump strainers.

#### Draw a water sample from the system and send it to out laboratory for analysis.

#### If the laboratory report is satisfactory, the system must then be treated with the appropriate formula.

### Glycol Systems:

#### In addition to procedures specified above perform procedures specified herein.

#### Test to prove concentration will prevent freezing to minus 40o C. Test inhibitor strength and include in procedural report. Refer to ASTM E202.

### Steam Systems: In addition to general requirements as specified above, perform following:

#### Remove internal components of steam traps until flushing and warm-up have been completed.

#### Open drip points to atmosphere. If needed for protection of personnel or environment, install flexible hose and direct discharge to safe location.

#### Starting at drip point closest to source, verify removal of condensate, then re-install steam trap internal parts. Repeat sequence down the line.

#### Water hammer: Determine source and eliminate cause.

### Steam boilers:

#### Isolate boilers from piping system.

#### Fill to normal operating level. Add cleaner. Fire to 50% of design operating steam pressure. Maintain for 24 h, during which blow down boiler every 4 h including water columns, controls, skimmer lines and valves, test cocks, blowdown valves. Add water to return to operating level.

#### Allow boiler to cool, then drain, flush and inspect.

#### Reconnect to piping system.

#### Refill boiler with clean softened water and immediately add chemical inhibitors.

#### Apply heat slowly and raise to normal design operating steam pressure. Maintain for 4 h.

#### Discharge condensate from steam system to sewer for 96 h after initial operation. During this period continue chemical treatment of boilers with inhibitors to ensure complete removal of oils, grease and millscale from steam and condensate return piping steam.

#### Drain steam condensate until it is clean and free from suspended matter. Ensure proper operation of steam traps.

#### Allow boiler to cool, drain, open inspection ports and wash out with clean water.

#### If boiler is not to be used immediately, refill with softened water, add sodium sulphite, bring up to pressure. Test for residual sulphite.

#### After cleaning is completed and system is filled, perform relevant start-up procedures as specified for hydronic systems:

Start-up of Hydronic Systems

### After cleaning is completed and system is filled:

#### Establish circulation and expansion tank level, set pressure controls.

#### Ensure air is removed.

#### Check pumps to be free from air, debris, possibility of cavitation when system is at design temperature.

#### Dismantle system pumps used for cleaning, inspect, replace worn parts, install new gaskets and new set of seals.

#### Clean out strainers repeatedly until system is clean.

#### Commission water treatment systems as specified in Section 23 25 00 - HVAC Water Treatment.

#### Check water level in expansion tank with cold water with circulating pumps OFF and again with pumps ON.

#### Repeat with water at design temperature.

#### Check pressurization to ensure proper operation and to prevent water hammer, flashing, cavitation. Eliminate water hammer and other noises.

#### Bring system up to design temperature and pressure slowly over a 48 hour period.

#### Perform TAB as specified in Section 23 05 93 - Testing, Adjusting and Balancing (TAB).

#### Adjust pipe supports, hangers, springs as necessary.

#### Monitor pipe movement, performance of expansion joints, loops, guides, anchors.

#### If sliding type expansion joints bind or if bellows type expansion joints flex incorrectly, shut down system, re-align, repeat start-up procedures.

#### Re-tighten bolts, etc. using torque wrench, to compensate for heat-caused relaxation. Repeat several times during commissioning.

#### Check operation of drain valves.

#### Adjust valve stem packings as systems settle down.

#### Fully open all balancing valves (except those that are factory-set).

#### Check operation of over-temperature protection devices on circulating pumps.

#### Adjust alignment of piping at pumps to ensure flexibility, adequacy of pipe movement, absence of noise or vibration transmission.

## cleaning

### Provide in accordance with Section 01 74 00 – Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION