# GENERAL

## SUMMARY

### Section Includes:

#### Materials and installation procedures for electric heating and cooling controls.

## Related Sections:

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

## REFERENCES

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (MSDS).

## SUBMITTALS

#### Product Data:

##### Submit manufacturer’s printed product literature, specifications and datasheet in accordance with Section 01 33 00 – Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 – Submittal Procedures.

#### Quality assurance submittals: submit following in accordance with Section 01 33 00 – Submittal Procedures.

##### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

##### Instructions: submit manufacturer’s installation instructions.

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 – Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer’s written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

# Products

## Thermostat (Line Voltage-Heating and Cooling)

### Line voltage, wall-mounted thermostat, for heating or cooling or heating-cooling as indicated with:

#### Full load rating: 6 A at 120 V.

#### Temperature setting range: 5° C to 30° C.

#### Thermometer range: 5° C to 30° C.

#### Markings in 5 degree increments.

#### Differential temperature fixed at 1.1° C.

## Thermostat (Heavy-Duty, Line Voltage, Heating and Cooling)

### Heavy-duty line voltage thermostat for heating, cooling, heating/cooling with manual changeover two- stage heating or coolingheating/cooling automatic changeover as indicated with:

#### Full load rating: 16 A at 120 V.

#### Temperature setting range: 5° C to 30° C.

#### Thermometer range: 5° C to 30° C.

#### Markings in 5 o degree increments.

#### Differential temperature fixed at 1.1° C.

## Thermostat (Line Voltage, Heating)

### Line voltage wall mounted integral electric heating thermostat with:

#### Full load rating: 22 A at 120 V.

#### Temperature setting range: 5° C to 30° C.

#### Single pole.

#### Thermometer range: 5° C to 30° C.

#### Scale markings: Off-5-10-15-20-25° C.

## Thermostat (Low Voltage)

### Low voltage wall thermostat:

#### For use on 24 V circuit at 1.5 A capacity.

#### With heat anticipator adjustable 0.1 to 1.2 A.

#### Temperature setting range: 10° C to 25° C.

#### Without sub-base.

## Thermostat (Remote Bulb)

### Line voltage remote bulb type thermostat with:

#### 30 A rating on 120 V.

#### 3 m copper capillary tube.

#### Moisture and dust-resistant enclosure.

## Thermostat (Fan Coil)

### Line voltage fan coil heating-cooling thermostat with:

#### Full load rating: 6 A at 120 V.

#### Two rocker switches for "Heat-Off-Cool" and "Low-Medium-High" fan switching. Isolate heating and cooling circuits. "Off" switch to break power to fan and thermostat.

## Thermostat Guards

### Thermostat guards: lockable, clear opaque plastic cast metal. Slots for air circulation to thermostat.

## Low Limit Temperature Alarm

### Low limit temperature alarm with:

#### Rating: 10.2 A at 120 V.

#### Sensing bulb and 6 m long capillary tube.

#### Switching action: manual reset.

#### Temperature setting range: 0° C to 15° C.

## High Limit Temperature Alarm

### High limit temperature alarm with:

#### Rating 10 A at 120 V 6 A at 240 V.

#### Positive lock-out.

#### Manual reset only after 14 C drop-in temperature.

#### Cutout setting: 50° C.

## Sail Switch

### Sail switch, mercury bulb type with stainless steel sail 79 mm width, adjustable range set for 3.8 m/s air velocity with upward flow.  Full load: 16 A at 120 V. Maximum ambient temperature: 82° C.

### Flow switch for  water or glycol, pipe size as indicated, CSA Enclosure l, rated at 16 A at 120 V. Maximum liquid temperature: 121° C. Maximum liquid gauge pressure of 1034 kPa ambient temperature range 0° C and 82° C. Ensure flow rate can activate flow switch at its minimum flow setting.

## Pressure Switch

### Pressure switch for water, steam, air at range to suit application with auto manual reset, contacts open on rise. Maximum allowable gauge pressure of 1.2 MPa. Full load 16 A at 120 V, ULC rated.

## TEMPERATURE SENSORS

### Temperature sensors supplied, installed and wired by Division 25.  Component of EMCS System.  Electrical Division to provide box and conduit to ceiling space only.

## Electric Heating Relays

### Low voltage solid state electric heating relays installed in ventilated enclosure, recess mounted, complete with power supply.  Complete assembly to be CSA approved.

### Heating relays, c/w integral heat sink, over voltage protection and status LED.

### Relay to have veiled conductor connections.  No exposed terminals permitted.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install control devices.

### On outside wall, mount thermostats on bracket or insulated pad 25 mm from exterior wall.

### Install remote sensing device and capillary tube in metallic conduit. Conduit enclosing capillary tube must not touch heater or heating cable.

## Cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION