# General

## SUMMARY

### Section includes:

#### Materials and installation for light fuel oil piping from oil tanks to boilers or engines.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

### Section 23 05 23.01 – Valves - Bronze.

### Section 23 08 01 – Performance Verification of Mechanical Piping Systems.

### Section 23 08 02 – Cleaning and Start-Up of Mechanical Piping Systems.

### Section 33 56 13 – Aboveground Fuel Storage Tanks

## References

### American Society of Mechanical Engineers (ASME)

#### ASME-B16.3, Malleable-Iron Threaded Fittings.

#### ASME-B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

### American Society for Testing and Materials (ASTM)

#### ASTM A47/A47M, Standard Specification for Ferritic Malleable Iron Castings.

#### ASTM A53/A53M, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

#### ASTM B61,Standard Specification for Steam or Valve Bronze Castings.

#### ASTM B75M, Standard Specification for Seamless Copper Tube.

### Canadian Standards Association (CSA)

#### CAN/CSA-B139, Installation Code for Oil Burning Equipment.

#### CAN/CSA-B140.0, General Requirements for Oil Burning Equipment.

### Health Canada/Workplace Hazardous Materials Information Systems

#### Safety Data Sheets (SDS)

### Manufacturers Standardization Society of the Valve and Fitting Industry (MSS)

#### MSS-SP-80, Bronze Gate, Globe, Angle and Check Valves.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 – Submittal Procedures

### Product Data

#### Submit manufacturer’s printed product literature, specifications and datasheet for piping, fittings and equipment.

##### Indicate on manufacturer’s catalogue literature the following:  valves

### Submit WHMIS SDS in accordance with Section. Indicate VOC’s for adhesive and solvents during application and curing Section 01 33 00 - Submittal Procedures.

### Test Reports:  submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

### Certificates:  submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions:  submit manufacturer’s installation instructions.

### Closeout submittals:  submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals

## QUALITY ASSURANCE

### Pre-Installation Meeting:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation and substrate conditions

##### Co-ordination with other building subtrades.

##### Review manufacturer’s installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06– Health and Safety Requirements.

### Trades people to have journeyperson qualifications.

## delivery, storage and handling

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers, steel, metal, plastic waste in accordance WMP.

#### Place materials defined as hazardous or toxic in designated containers.

#### Handle and dispose of hazardous materials in accordance with Canadian Environmental Protection Act (CEPA), Transportation of Dangerous Goods Act (TDGA), Regional and Municipal regulations.

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

#### Unused paint, coating materials must be disposed of at official hazardous material collection site as approved by Owner.

#### Unused sealant materials must not be disposed of into sewer system, into streams, lakes, onto ground or in other location where it will pose health or environmental hazard.

# Products

## Fill, Vent and Carrier Pipe (Above Ground)

### Steel: to ASTM A53/A53M, Schedule 40, continuous weld or electric resistance welded, screwed.

### Copper: type K, soft copper tubing, to ASTM B75M, in continuous lengths.

## Steel Pipe Coating

### Bituminous paint: in accordance with manufacturer's recommendations for exterior above ground or galvanized.

## Jointing Material

### Screwed fittings: Teflon or pulverized lead paste. In accordance with manufacturers recommendations.

### Soldered fittings:  95/5.

## Fittings

### Steel:

#### Malleable iron: screwed, banded, Class 150 to ASME-B16.3.

#### Welding: butt-welding to ASME-B16.9.

#### Unions: malleable iron, brass to iron, ground seat, screwed, to ASTM A47/A47M.

#### Nipples: Schedule 40, to ASTM A53/A53M.

### Copper:

#### Piping: soldered type.

#### Connections to equipment: flared.

## Gate Valves

### NPS 2 and under, screwed bonnet:

#### Rising stem: to MSS-SP-80, Class 125, 860 kPa, bronze body, solid wedge disc as specified under Section 23 05 23.01 – Valves - Bronze.

## Globe Valves

### NPS 2 and under, screwed:

#### To MSS-SP-80, Class 125, 860 kPa, bronze body, screwed over bonnet, renewable bronze disc as specified under Section 23 05 23.01 – Valves – Bronze.

## Ball Valves

### NPS 2 and under:

#### Bronze body, screwed ends, TFE seal, hard chrome ball, 4 MPa, WOG as specified under Section 23 05 23.01 – Valves - Bronze.

## Swing Check Valves

### NPS 2 and under, screwed:

#### To MSS-SP-80, Class 125, 860 kPa, bronze body,  renewable composition disc suitable for oil service, screw in cap, regrindable seat as specified under Section 23 05 23.01 – Valves - Bronze

## Fuel Oil Transfer Pumps

### Two positive displacement self-priming, rotary gear or screw type, direct driven from TEFC motor, mounted on common base. Complete with mechanical seal, permanently sealed ball bearings, relief valve, compound gauge on inlet, pressure gauge on discharge

### Capacity:

#### Pumped fluid: #2 fuel oil.

#### Flow rate:  as indicated.

#### Motor: as indicated.

## Oil Filter

### Duplex type replaceable cartridge type as recommended by oil burner manufacturer.

### Furnish spare filter cartridge.

## Oil Meters

### Accuracy: tested and certified by manufacturer for accuracy within plus or minus 0.2% between 20% and 100% rated capacity.

### Capacity: as indicated.

## Anti-siphon Valve

### Each tank:  Automatic shut-off to prevent spillage in the event of line rupture, cast or ductile iron body, adjustable hydrostatic pressure, brass trim, corrosion-resistant steel spring, fluorocarbon seal, sized for application, built-in thermal expansion pressure relief valve.

## FUSIBLE VALVE

### Gate or globe type, gate type preferred, with spring and replaceable fusible element at 74°C, also manually operable.

## FOOT VALVES

### Provide and install on the tank suction stub a double poppet foot valve of bronze construction, with lapped-in seats, stem guided poppets and 20 mesh monel screen.  At the tank suction stub exit install a foot valve extractor.

# Execution

## Piping

### Install oil piping system in accordance with CAN/CSA-B139 and CAN/CSA-B140.0.

### Slope piping down in direction of storage tank unless otherwise indicated.

### Suction and return piping inside building (above ground):

#### Steel, with screwed fittings in trench below floor or run on floor protected by 6 mm checkered aluminum plate cover in traffic areas.

#### Install filter and gate valve at burners.

#### Where suction line enters building, install union, gate valve, anti-syphon device and cap (for priming purposes).

### Fill, vent, suction and return outside building: (above ground).

#### Steel piping welded throughout except at tanks where use electrically isolating fittings.

#### Grading: slope piping at 1% minimum back to tanks.

### Install suction and return buried piping in outer casings in accordance with provincial regulations and Section 33 56 13 – Aboveground Fuel Storage Tanks.

### Piping at tanks:

#### Suction: terminate 150 mm from bottom of tank with foot valve.

#### Return: terminate 100 mm from bottom of tank with return bend.

#### Vent: vent whistle. Terminate open end 3600 mm above grade with return bend, vent alarm and removable 10 mesh copper screen.

#### Fill: terminate as indicated with liquid-tight and vapourproof cover and locking cap, chain and padlock.

#### Dipstick: extend tube to within 150 mm from bottom of tank. Terminate at grade with cap and chain and watertight cover.

### Interconnections between tanks:

#### Interconnect fill, vent, suction, and tank bottoms.

#### Valve to permit isolation of tanks without interfering with use of other tanks.

## Valves

### Install valves with stems upright or horizontal unless approved otherwise by Owner.

### Install ball valves at branch take-offs, to isolate pieces of equipment and as indicated.

### Install globe valves for balancing and in by-pass around control valves.

### Install swing check valves on discharge of pumps and as indicated.

## Oil Transfer Pumps

### Install as indicated.

### Install gate valves on inlet and discharge connections.

### Install pressure gauge at pump discharge, compound gauge on pump inlet connection.

### Install relief valve in pump discharge piping with relief valve discharge pipe to return line to tank.

## Oil Filters

### Install as indicated

### At time of Substantial Completion, replace filter cartridge with new.

## Overfill and Spill Protection

### See Section 33 56 13 – Aboveground Fuel Storage Tanks.

## Field Quality Control

### Site Tests/Inspection:

#### Test system in accordance with CSA-B139 and CSA-B140.0 and authorities having jurisdiction.

#### Isolate tanks from piping pressure tests.

#### Maintain test pressure during backfilling.

### Manufacturer’s Field Services:

#### Have manufacturer of products, supplied under this Section, review work involved in the handling, installation/application, protection and cleaning, of its products and submit written reports, in acceptable format, to verify compliance of work with contract.

#### Provide manufacturer’s field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer’s instructions.

#### Schedule site visits, to review work, at stages listed:

##### After delivery and storage of products, and when preparatory Work, or other Work, on which the work of this Section depends, is complete but before installation begins.

##### Twice during progress of work at 25% and 60% complete.

##### Upon completion of the work, after cleaning is carried out.

#### Obtain reports, within three (3) working days of review, and submit, immediately, to Owner.

### Refer to Section 23 08 01 – Performance Verification Mechanical Piping System

## Cleaning and Start-Up

### In accordance with Section 23 08 02 - Cleaning and Start-Up of Mechanical and Piping Systems, supplemented as specified herein.

### Flush after pressure test with number 2 fuel oil for a minimum of two hours. Clean strainers and filters.

### Dispose of fuel oil used for flushing out in accordance with requirements of authority having jurisdiction.

### Check vents from regulators, control valves are terminated in approved location and are protected against blockage and damage.

### Check entire installation is approved by authority having jurisdiction.

### Perform cleaning operations as specified in Section 01 74 00 – Cleaning and in accordance with manufacturer’s recommendations.

### On completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## Performance Verification/COMMISSIONING

### Refer to Section 23 08 01 – Performance Verification of Mechanical Piping Systems.

### Refer to Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION