# General

## SUMMARY

### Section Includes.

#### Materials and installation for steel piping, valves and fittings for hydronic systems in building services piping.

## Related Sections.

### Section 01 33 00 - Submittal Procedures.

### Section 01 35 29.06- Health and Safety Requirements.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 21 05 01 - Common Work Results -Mechanical.

### Section 23 05 00 – Common Work Results for Plumbing.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

### Section 23 05 17 - Pipe Welding.

### Section 23 05 23.01 - Valves - Bronze.

### Section 23 05 23.02 - Valves - Cast Iron

### Section 23 05 93 - Testing, Adjusting and Balancing for HVAC.

### Section 23 07 13 – Duct Insulation.

### Section 23 10 16 – HVAC Equipment Insulation.

### Section 23 07 19 – HVAC Piping Insulation.

### Section 23 08 01 - Performance Verification of Mechanical Piping.

### Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems.

## REFERENCES

### American Society of Mechanical Engineers (ASME).

#### ASME B16.1, Gray Iron Pipe Flanges and Flanged Fittings: Classes 25, 125, and 250.

#### ASME B16.3, Malleable Iron Threaded Fittings: Classes 150 and 300.

#### ASME B16.5, Pipe Flanges and Flanged Fittings: NPS   through NPS 24 Metric/Inch Standard.

#### ASME B16.9, Factory-Made Wrought Buttwelding Fittings.

#### ASME B18.2.1, Square Hex, Heavy Hex and Askew Head Bolts and Hex, Heavy Hex, Hex Flange. Loded Head and Lag Screws (Inch Series).

#### ASME B18.2.2, Nuts for General Applications: Machine Screw Nuts, Hex, Square, Hex Flange, and Coupling Nuts (Inch Series).

### American Society for Testing and Materials International, (ASTM).

#### ASTM A47/A47M, Standard Specification for Ferritic Malleable Iron Castings.

#### ASTM A53/A53M, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated Welded and Seamless.

#### ASTM A536, Standard Specification for Ductile Iron Castings.

#### ASTM B61, Standard Specification for Steam or Valve Bronze Castings.

#### ASTM B62, Standard Specification for Composition Bronze or Ounce Metal Castings.

#### ASTM E202, Standard Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

### American Water Works Association (AWWA).

#### AWWA C111, Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings.

### Canadian Standards Association (CSA International).

#### CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

#### CAN/CSA W48, Filler Metals and Allied Materials for Metal Arc Welding.

### Manufacturer's Standardization of the Valve and Fittings Industry (MSS).

#### MSS-SP-67, Butterfly Valves.

#### MSS-SP-70, Cast Iron Gate Valves, Flanged and Threaded Ends.

#### MSS-SP-71, Cast Iron Swing Check Valves Flanged and Threaded Ends.

#### MSS-SP-80, Bronze Gate, Globe, Angle and Check Valves.

#### MSS-SP-85, Cast Iron Globe and Angle Valves, Flanged and Threaded Ends.

### Province of Newfoundland and Labrador Boiler, Pressure Vessel and Compressed Gas Regulations.

## SUBMITTALS

### Submit shop drawings in accordance with Section 01 33 00 – Submittal Procedures.

### Closeout Submittals.

#### Provide maintenance data for incorporation into manual specified in Section    01 78 00 – Closeout Submittals, and include the following:

##### Special servicing requirements.

### Grooved joint couplings and fittings to be indicated on product submittals and to be specifically identified with the applicable style or series designation.

### Grooved products manufacturer to supply on site tools and products for installation training.

### All grooved products to be of one manufacturer.

### Groove products to have current CRN numbers.

## QUALITY ASSURANCE

### Health and Safety.

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal.

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

## MAINTENANCE

### Extra Materials.

#### Provide following spare parts:

##### Valve seats: one for every ten valves, each size. Minimum one.

##### Discs: one for every ten valves, each size. Minimum one.

##### Stem packing: one for every ten valves, each size. Minimum one.

##### Valve handles: two of each size.

##### Gaskets for flanges: one for every ten flanges.

# Products

## PIPE

### Steel pipe: to ASTM A53/A53M, Grade B as follows:

#### To NPS 6: schedule 40.

#### NPS 8 and 10: schedule 40.

#### NPS 12 and over, 10 mm wall thickness.

## PIPE JOINTS

### NPS 2 and under: screwed fittings with PTFE tape or lead-free pipe dope.

### NPS 2-1/2 and over: welding fittings and flanges to CAN/CSA W48.

### Roll grooved:  rigid coupling to CSA B242.

### Flexible couplings to CSA B242 to be used where noted on drawings and on elbows utilized on expansion joints.

### Flanges: plain ASME, B16.1, raised face, slip-on or weld neck to ASME B16.5.

### Orifice flanges: slip-on raised face, 2100 kPa.

### Flange gaskets: to AWWA C111

### Pipe thread: taper.

### Bolts and nuts: to ASME B18.2.1 and ASME B18.2.2.

### Roll grooved coupling gaskets: NPS 2 to 8, type EHP, EPDM high performance, -40°C to +120°C for continuous operation, NPS 10 and above type EPDM, -30°C to +110°C for continuous acceptable on hot hater, glycol water, chilled water and condenser water.

## FITTINGS

### Screwed fittings: malleable iron, to ASME B16.3, Class 150.

### Pipe flanges and flanged fittings:

#### Cast iron: to ASME B16.1, Class 125.

#### Steel: to ASME B16.5.

### Butt-welding fittings: steel, to ASME B16.9.

### Unions: malleable iron, to ASTM A47/A47M and ASME B16.3.

### Fittings for roll grooved piping: malleable iron to ASTM A47/A47M, ductile iron to ASTM A536.

## VALVES

### Connections:

#### NPS2 and smaller: screwed ends.

#### NPS2.1/2 and larger: Flanged or grooved ends.

### Gate valves: to MSS-SP-70 and MSS-SP-80 Application: Isolating equipment, control valves, pipelines:

#### NPS 2 and under:

##### Mechanical Rooms: Class 125 rising stem, solid wedge disc, as specified Section 23 05 23.01 – Valves – Bronze.

##### Elsewhere: Class 125, non- rising stem, solid wedge disc, as specified Section 23 05 23.01 – Valves – Bronze.

#### NPS 21/2 and over:

##### Mechanical Rooms: rising stem, solid wedge disc, lead free bronze trim, as specified Section 23 05 23.02 – Valves – Cast Iron.

##### Elsewhere: Non- rising stem, solid wedge disc, lead free bronze trim, as specified Section 23 05 23.02 – Valves – Cast Iron.

### Butterfly valves: to MSS-SP-67 Application: Isolating cells or section of multiple component equipment (eg. multi-section coils, multi-cell cooling towers).

#### NPS 2 1/2 and over: Lug type or Grooved ends: as specified Section 23 05 17 – Pipe Welding.

### Globe valves: to MSS-SP-80 and 85 Application: Throttling, flow control, emergency bypass.

#### NPS 2 and under:

##### Mechanical Rooms: with plug disc, as specified Section 23 05 23.01 – Valves – Bronze.

##### Elsewhere: Globe, with composition disc, as specified Section 23 05 23.01 – Valves - Bronze.

#### NPS 2 1/2 and over:

##### With composition bronze disc, bronze trim, as specified Section 23 05 23.02 – Valves – Cast Iron.

### Balancing, for TAB:

#### Sizes: Calibrated balancing valves, as specified this section.

#### NPS 2 and under:

##### copper alloy body threaded and, 2.1 MPa rating, globe style, self sealing measuring ports for temperature or pressure probes, locking tamper proof setting.

##### Mechanical Rooms and Elsewhere: Globe, with plug disc as specified Section 23 05 23.01 - Valves – Bronze.

##### In lieu of standard malleable iron or copper fittings the Contractor may install the following component system:

###### Union port fitting with air vent and pressure/temperature port.

###### Balancing valve, strainer with drain valve, ball valve combination may also be used.

#### NPS 2 ½  and over:

##### Ductile iron body, flanged or grooved connections, 1700 kPa rating minimum, globe style, self sealing measurement parts for temperature or pressure probes, locking tamper proof setting.

### Drain valves: Gate, Class 125 non-rising stem, solid wedge disc, as specified Section 23 05 23.01 – Valves - Bronze.

### Bypass valves on gate and globe valves NPS 8 and larger: NPS ¾ as specified Section 23 05 23.01 – Valves - Bronze.

### Swing check valves: to MSS-SP-71.

#### NPS 2 and under:

##### Class 125 swing, with composition disc, as specified Section 23 05 23.01 – Valves - Bronze.

#### NPS 2 1/2 and over:

##### Flanged or grooved ends: as specified Section 23 05 23.02 – Valves – Cast Iron.

### Silent check valves:

#### NPS 2 and under:

##### As specified Section 23 05 23.01 – Valves – Bronze.

#### NPS 2 1/2 and over:

##### Flanged or grooved or wafer style ends: as specified Section 23 05 23.02 – Valves – Cast Iron.

### Ball valves:

#### NPS 2 and under: as specified Section 23 05 23.01 – Valves - Bronze.

### Glycol

#### Ethylene glycol with inhibitors for corrosion control.

#### Percent by volume as indicated.

# Execution

## PIPING INSTALLATION

### Install pipework in accordance with Section 23 05 15 - Common Installation Requirements for HVAC Pipework by certified journeyperson and authority having jurisdiction.

## CIRCUIT BALANCING VALVES

### Install flow measuring stations and flow balancing valves as indicated.

## CLEANING, FLUSHING AND START-UP

### In accordance with Section 23 08 02 – Cleaning and Start-up of Mechanical Piping Systems.

## TESTING

### Test system in accordance with Section 21 05 01 – Common Work Results - Mechanical.  Minimum 1.5 times working pressure or 1000 kPa.

### For glycol systems, retest with ethylene glycol to ASTM E202, inhibited, for use in building system after cleaning. Repair leaking joints, fittings or valves.

## BALANCING

### Balance water systems to within plus or minus 5 % of design output.

### Refer to Section 23 05 93 – Testing, Adjusting and Balancing for HVAC, for applicable procedures.

## GLYCOL CHARGING

### Provide mixing tank and positive displacement pump for glycol charging.

### Retest for concentration to ASTM E202 after cleaning.

## PERFORMANCE VERIFICATION

### In accordance with Section 23 08 01 – Performance Verification of Mechanical Systems.

### Provide copies of test reports for Commissioning Manuals.

END OF SECTION