# General

## summary

### Section includes:

#### The supply and installation of hydronic specialties equipment.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06– Health and Safety Requirements

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 01 78 00 – Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

### Section 23 08 01 – Performance Verification of Mechanical Piping Systems.

## References

### American Society of Mechanical Engineers (ASME)

#### ANSI/ASME, Boiler and Pressure Vessels Code.

### American Society for Testing and Materials (ASTM)

#### ASTM A47/A47M, Specification for Ferritic Malleable Iron Castings.

#### ASTM A48, Standard Specification for Gray Iron Castings.

#### ASTM A216, Standard Specification for Steel Castings, Carbon, Suitable for Fusion Welding, For high Temperature Service.

#### ASTM A278M, Specification for Gray Iron Castings for Pressure-Containing Parts for Temperatures up to 345° C.

#### ASTM A516/A516M, Specification for Pressure Vessel Plates, Carbon Steel, for Moderate and Lower Temperature Service.

#### ASTM A536, Specification for Ductile Iron Castings.

#### ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

### Canadian Standards Association (CSA)

#### CSA B51, Boiler, Pressure Vessel, and Pressure Piping Code.

### Provincial Boiler, Pressure Vessel and Compressed Gas Regulations.

## submittals

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:  Submit WHMIS SDS – Safety Data Sheets.

#### Submit shop drawings and product data in accordance with Section 01 33 00 - Submittal Procedures.

#### Indicate on product data expansion tanks, air vents, separators, valves, and strainers.

### Closeout Submittals:

#### Submit maintenance data in accordance with Section 01 78 00 – Closeout Submittals.

## quality Assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## delivery storage and disposal

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

# Products

## Canadian Registration Numbers (CRN)

### Required on all products as per Provincial Regulations and CSA B51.

## Diaphragm Type Expansion Tank

### Horizontal or vertical as indicated steel pressurized diaphragm type expansion tank.

### Capacity: as indicated

### Size: length and diameter as indicated.

### Diaphragm sealed in elastomer or EPDM suitable for 115°C operating temperature.

### Working pressure: 860 kPa with ASME stamp and certification.

### Air precharged to 84 kPa (initial fill pressure of system) or as indicated.

### Saddles for horizontal installation, base mount for vertical installation.

### Supports: Provide supports with hold down bolts and installation templates.

### Renewable diaphragm.

## Automatic Air Vent

### Standard float vent: brass body and NPS 1/8 connection and rated at 1000 kPa working pressure.

### Industrial float vent: ASTM A48 Class 30 cast iron body and NPS 1/2 connection and rated at minimum 860 kPa working pressure.

### Float: solid material suitable for 115°C working temperature.

## Air Separator - Boiler Mounted

### Complete with dip tube.

### Working pressure: 860 kPa.

## Air Separator - Expansion Tank Fitting

### Complete with adjustable vent tube and built-in manual vent valve.

### Working pressure: 860 kPa.

## Air Separator - In-Line

### Working pressure: 860 kPa.

### Size: for 0.15 m/s

### Shell:  steel to ASME BPVC Section VIII.

### Removable stainless steel collection tube.

## Combination Separators/Strainers

### Steel, tested and stamped in accordance with ANSI/ASME BPVC, for 860 kPa operating pressure, with stainless steel integral strainer with 5.0 mm perforations, tangential inlet and outlet connections, and internal stainless steel air collector tube.

## Combination Low Pressure Relief and Reducing Valve

### Adjustable pressure setting: 206 kPa relief, 55 to 172 kPa reducing or as indicated.

### Low inlet pressure check valve.

### Removable strainer.

## Pipe Line Strainer

### NPS 1/2 to 2: 1.7 MPa steam non-shock bronze body to ASTM B62, screwed or grooved connections, Y pattern.

### NPS 2 1/2 to 12: Class 150 cast steel body to ASTM A216 GR.WCB or cast iron body Class 125 to ASTM-A48, Class 30, flanged connections.

### NPS 2 to 12: T type 2.1 MPa with ductile iron body to ASTM A536 or malleable iron body to ASTM A47M, grooved ends.

### Blowdown connection: NPS 1.

### Screen: stainless steel with 1.19 mm perforations.

### Working pressure: 860 kPa.

## Suction Diffuser

### Body: cast iron with flanged or grooved ductile iron connections 2.1 MPa.

### Strainer: with built-in, disposable 1.19 mm mesh, start-up strainer, low pressure drop screen and NPS 1 blowdown connection.

### Permanent magnet particle trap.

### Full length straightening vanes.

### Pressure gauge tappings.

### Adjustable support leg.

## Triple Duty Valve

### Center-guided non-slam drip tight check valve.

### Positive shut-off valve.

### Calibrated system balance valve.

### Straight pattern as indicated.

### Flanged or Grooved end connections.

### Soft seat design for positive sealing.

### Construction:

#### Body:  cast iron with bronze seat.

#### Disc:  bronze with EPDM seat insert.

#### Stem:  stainless steel.

#### Spring:  stainless steel.

#### Packing:  Teflon-Graphite (Asbestos-free).

#### Gasket:  asbestos-free.

#### Readout valve:  brass with EPT insert, check valve and gasket.

### Maximum operating temperature:  121ºC.

### Maximum working pressure:  1.2 MPa.

### Valve design shall permit repacking under full system pressure.

### Provide complete with brass readout valves, with integral check feature, to facilitate taking differential pressure readings across the orifice for accurate system balance.

### Provide CV rating at 10% increments.  Manufacturer shall supply the CV rating for read-out of flow determination and system pressure drop.

### Capacity: see schedule on drawings for performance criteria and model selections.

# Execution

## General

### Install as indicated and to manufacturer's recommendations.

### Run drain lines and blow off connections to terminate above nearest drain.

### Maintain proper clearance to permit service and maintenance.

### Should deviations beyond allowable clearances arise, request and follow Owner’s directive.

### Check shop drawings for conformance of all tappings for ancillaries and for equipment operating weights.

## Strainers

### Install in horizontal or down flow lines.

### Ensure clearance for removal of basket.

### Install ahead of each pump.

### Install ahead of each automatic control valve larger than NPS 1 and radiation and as directed.

## AIR VENTS

### Install at high points of systems.

### Install gate valve on automatic air vent inlet. Run discharge to nearest drain or service sink.

## Expansion Tanks

### Adjust expansion tank pressure to suit design criteria.

### Install lockshield type valve at inlet to tank.

## Pressure Safety Relief Valves

### Run discharge pipe to terminate above nearest drain.

## Suction Diffusers

### Install on inlet to pumps having suction size greater than 50.

## Performance Verification

### In accordance with Section 23 08 01 - Performance Verification of Mechanical Piping Systems, supplemented as specified herein.

### Provide copies of test reports for Commissioning Manuals.

END OF SECTION