# General

## section includes

### Materials, equipment selection, installation and start up for hydronic system pumps.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal

### Section 01 35 29.06- Health and Safety Requirements.

### Section 01 78 00 - Closeout Submittals.

## References

### American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE).

#### Standard 90.1, Energy Standard for Buildings Except Low-Rise Residential Buildings.

### National Energy Code of Canada for Buildings (NECB).

### Canadian Standards Association (CSA International).

#### CAN/CSA-B214, Installation Code for Hydronic Heating Systems.

### National Electrical Manufacturer’s Association (NEMA)

#### NEMA MG 1, Motors and Generators.

### American National Standards Institute/Hydraulics Institute (ANSI/HI)

#### ANSI/HI 1.3, Rotodynamic (Centrifugal) Pumps for Design and Application.

## submittals

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Submit shop drawings and product data in accordance with Section 01 33 00 - Submittal Procedures.

### Submit manufacturer's detailed composite wiring diagrams for control systems showing factory installed wiring and equipment on packaged equipment or required for controlling devices or ancillaries, accessories and controllers.

### Submit product data of pump curves for review showing point of operation.

### Indicate piping, valves and fittings shipped loose by packaged equipment supplier, showing their final location in field assembly.

### Provide maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## Health and safety

### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## waste management and disposal

### Separate waste material for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Separate for reuse and recycling and place in designated containers, steel, metal, plastic waste in accordance with Waste Management Plan.

### Fold up metal banding, flatten and place in designated area for recycling.

## Extra Materials

### Provide maintenance materials in accordance with Section 01 78 00 - Closeout Submittals.

### Furnish following spare parts:

#### Mechanical seal for each pump.

#### Packing for each pump.

#### Set of gaskets for each pump.

# Products

## equipment

### Do component selection and sizing to CAN/CSA-B214.

## In-Line Circulators

### Volute: cast iron radially split, with screwed or flanged design suction and discharge connections.

### Impeller: alloy steel, cast bronze, or cast iron to suit application.

### Shaft:  stainless steel with bronze sleeve bearing, integral thrust collar.

### Seal assembly: mechanical for service to 135 0C.

### Coupling: flexible self-aligning.

### Motor: as per Section 23 05 13 – Common Motor Requirements for HVAC Equipment and as per manufacturer’s recommendations. Speed and power as indicated in the pump schedule.

### Capacity: as indicated in the pump schedule.

### Design pressure: 1200 kPa.

## IN-line wet rotor circulators

### Pump body:  Cast iron

### Impellor:  polypropylene (glass filled)

### Shaft:  stainless steel

### Bearings:  Graphite

### Gasket material:  EPDM.

### Maximum fluid temperature:  110o C.

### Maximum working pressure:  1000 kPa.

### Capacity:  as indicated in pump schedule.

### Connections:  union or flanged.

## Vertical In-Line Circulators

### Volute: cast iron radially split, with tapped openings for venting, draining and gauge connections, with screwed or flanged suction and discharge connections.

### Impeller: bronze or cast iron, dynamically balanced.

### Shaft: stainless steel with bronze sleeve bearing, integral thrust collar.

### Seal assembly: outside balanced, mechanical for service to 1350 C.  Flush line fittings to include 50 micron filter and sight flow indicator, if pump differential exceeds 200 kPa replace filter with cyclone type separator.

### Coupling: flexible self-aligning.

### Motor: NEMA base, drip proof, ball bearing as per Section 23 05 13 – Common Motor Requirements for HVAC Equipment, speed and power as indicated in pump schedule.

### Capacity: as indicated in pump schedule.

### Design pressure: 1200 kPa.

## Single SUCTION Centrifugal Pump

### General: all iron pump complete with motor.

### Base: common cast iron or fabricated steel with drip rim and tapping for drain connection.

### Volute: cast iron radially split, back pull out end suction, screwed or flanged suction and discharge, with drain plug and vent cock, suction and discharge pressure gauge tappings.

### Impeller:  cast iron or stainless steel enclosed type, keyed drive with locking nut or screw, dynamically balanced.

### Shaft: stainless steel with two point support for ball bearing mounting hardened wear rings at packing gland.

### Seal assembly: mechanical seal, oil or grease lubricated. On open system flush line with 50 micron filter and site flow indicator.  When differential exceeds 200 kPa use cyclone type separator.

### Coupling: flexible self-aligning complete with coupling guard.

### Motor: NEMA Class B, squirrel cage induction, premium efficiency continuous duty, drip proof, ball bearing, maximum temperature rise 500 C,  as per Section 23 05 13 - Common Motor Requirements for HVAC Equipment, speed and power as indicated in pump schedule.

### Capacity: as indicated in pump schedule.

### Design pressure: 1200 kPa.

## Horizontal split case Centrifugal Pump

### General:  all iron pump complete with motor.

### Base: common cast iron or fabricated steel base with drip rim and tapping for drain connection.

### Volute: cast iron horizontally split, with suction and discharge nozzles integrally cast in lower half, flanged suction and discharge, with drain plug and vent cock, suction and discharge pressure tappings.

### Impeller: bronze enclosed type, keyed drive.

### Shaft: alloy steel stainless steel with two point support for ball bearing mounting hardened wear rings at packing gland.

### Seal assembly: mechanical seal, oil or grease lubricated. On open system flush line with 50 micron filter and site flow indicator, when differential exceeds 200 kPa cyclone type separator.

### Coupling: flexible self-aligning complete with coupling guard.

### Motor: NEMA Class B, squirrel cage induction, speed and power as indicated in pump schedule, continuous duty, drip proof, ball bearing, maximum temperature rise 500 C, premium efficiency, as per Section 23 05 13 - Common Motor Requirements for HVAC Equipment.

### Capacity: as indicated in pump schedule.

### Design pressure: 1200 kPa.

# Execution

## Installation

### In line circulators: install as indicated by flow arrows. Support at inlet and outlet flanges or unions. Install with bearing lubrication points accessible.

### Base mounted type: supply templates for anchor bolt placement. Furnish anchor bolts with sleeves. Place level, shim unit and grout. Align coupling in accordance with manufacturer's recommended tolerance. Check oil level and lubricate.

### Ensure that pump body does not support piping or equipment. Provide stanchions or hangers for this purpose. Refer to manufacturer's installation instructions for details.

### Pipe drain tapping to floor drain.

### Install volute venting pet cock in accessible location.

### Check rotation prior to start-up.

### Install pressure gauge ball valves.

## Start-up

### General

#### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements, supplemented as specified herein.

#### In accordance with manufacturer's recommendations.

### Procedures:

#### Before starting pump, check that cooling water system, over-temperature and other protective devices are installed and operative.

#### After starting pump, check for proper, safe operation.

#### Check installation, operation of mechanical seals, packing gland type seals. Adjust as necessary.

#### Check base for free-floating, no obstructions under base.

#### Run-in pumps for 12 continuous hours.

#### Verify operation of over-temperature and other protective devices under low- and no-flow condition.

#### Eliminate air from scroll casing.

#### Adjust water flow rate through water-cooled bearings.

#### Adjust alignment of piping and conduit to ensure true flexibility at all times.

#### Eliminate cavitation, flashing and air entrainment.

#### Adjust pump shaft seals.

#### Measure pressure drop across strainer when clean and with flow rates as finally set.

#### Replace seals if pump used to degrease system or if pump used for temporary heat.

#### Verify lubricating oil levels.

## Performance Verification (PV) and Commissioning

### General

#### In accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements, supplemented as specified herein.

#### In accordance with manufacturer's recommendations.

### Assumptions: These PV procedures assume that:

#### Manufacturer's performance curves are accurate.

#### Valves on pump suction and discharge provide tight shut-off.

### Net Positive Suction Head (NPSH):

#### Application: Measure NPSH for pumps which operate on open systems and with water at elevated temperatures.

#### Measure using procedures prescribed in the ANSI/HI 1.6.

#### Where procedures do not exist, discontinue PV, report to Owner and await instructions.

### Multiple Pump Installations - Series and Parallel:

#### Repeat PV procedures specified above for pump performance and pump BHP for combinations of pump operations.

### Mark points of design and actual performance at design conditions as finally set upon completion of TAB.

### Commissioning Reports: In accordance with Section 01 91 13.13 –Commissioning (Cx) Requirements Reports supplemented as specified herein. Reports to include:

#### Record of point(s) of actual performance at maximum and minimum conditions and for single and parallel operation as finally set at completion of commissioning on pump curves.

#### Report forms as specified Section 01 91 13.13 – Commissioning (Cx) Requirements.

#### Pump performance curves (family of curves).

END OF SECTION