# General

## summary

### Section Includes:

#### Materials and installation for copper tubing and fittings for refrigerant.

## Related Sections:

### Section 01 33 00 - Submittal Procedures.

### Section 01 35 29.06 - Health and Safety Requirements.

### Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 23 05 15 - Common Installation Requirements for HVAC Pipework.

## references

### American Society of Mechanical Engineers (ASME)

#### ASME B16.22, Wrought Copper and Copper Alloy Solder - Joint Pressure Fittings.

#### ASTM A307, Standard Specification for Carbon Steel Bolts and Studs, and Threaded Rod 60,000 PSI Tensile Strength.

#### ASME B16.26, Cast Copper Alloy Fittings for Flared Copper Tubes.

#### ASME B31.5, Refrigeration Piping and Heat Transfer Components.

### American Society for Testing and Materials (ASTM)

#### ASTM A 307, Standard Specification for Carbon Steel Bolts and Studs, 60,000 PSI Tensile Strength.

#### ASTM B 280, Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service.

### Canadian Standards Association (CSA)

#### CSA B52, Mechanical Refrigeration Code.

### Environment Canada (EC)

#### EPS1/RA/1, Environmental Code of Practice for the Elimination of Fluorocarbon Emissions from Refrigeration and Air Conditioning Systems.

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

### Province of Newfoundland and Labrador Boiler, Pressure Vessel and Compressed Gas Regulations

## submittals

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions: submit manufacturer's installation instructions.

### Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## quality assurance

### Pre-Installation Meeting:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation and substrate conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer's installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

### Trades people to be journeyperson and graduate from a recognized college refrigeration trade program.

## delivery, storage and handling

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers, steel, metal, plastic waste in accordance with Waste Management Plan (WMP).

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

# Products

## Tubing

### Processed for refrigeration installations, deoxidized, dehydrated and sealed.

#### Hard copper: to ASTM B280, type ACR B (nitrogenized).

#### Annealed copper: to ASTM B280, with minimum wall thickness as per CSA B52 and ASME B31.5.

## Fittings

### Service: design pressure 2070 kPa and temperature 121° C.

### Brazed:

#### Fittings: wrought copper to ASME B16.22.

#### Joints: silver solder, 45% Ag - 80% Cu - 5% P and non-corrosive flux for copper to steel or brass; Silfoss-15 for copper to copper.

### Flanged:

#### Bronze or brass, to ASME B16.24, Class 150 and Class 300, tongue and groove type.

#### Gaskets: suitable for service.

#### Bolts, nuts and washers: to ASTM A307, heavy series.

### Flared:

#### Bronze or brass, for refrigeration, to ASME B16.26.

## Pipe Sleeves

### Hard copper or steel, sized to provide 6.0 mm clearance between sleeve and uninsulated pipe or between sleeve and insulation.

## Valves

### 7/8 ODS and under: Class 500, 3.5 MPa, globe or angle non-directional type, diaphragm, packless type, with forged brass body and bonnet, moistureproof seal for below freezing applications, brazed connections.

### Over 7/8 ODS:  Class 375, 3 MPa, globe or angle type, diaphragm, packless type, back-seating, cap seal, with cast bronze body and forged brass bonnet, moisture-proof seal for below freezing applications, brazed connections, non-rotating, self aligning swivel disc, Teflon seat, -400 C - 1630 C.

### Ball valves 7 3/8 ODS to 3 1/8 ODS:  maximum WP 4MPa, -400 C to 1490 C, live loaded stem seal, double “O” ring hermetically sealed body, blowout proof stem, seal cap “O” ring sealed, valve position indicators, forged brass body bonnet, brass cap, triple sealed plated steel item, Teflon ball seals and gasket, extended copper connections, helium leak test to maximum 0.28 g/yr.

### Check valves 7/8 ODS to 3 1/8 ODS cast bronze body, brass bonnet, Teflon seat, internal parts removable minimum opening pressure 3.5 kPa, maximum WP 3.5 kPa - 290 C to 1490 C, UL and CSA approved.

### Check valves 3/8 ODS to 7/8 ODS: brass construction, Teflon seal, removable piston, maximum WP 3.5 kPa, -400 C to 1490 C, suitable for high side, low side and hot gas.  UL and CSA approved, maximum opening pressure 3.5 kPa.

# Execution

## manufacturer’s instructions

### Compliance:  comply with manufacturer’s written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## GENERAL

### In accordance with Section 23 05 15 - Common Installation Requirements for HVAC Pipework, supplemented as specified herein.

### Install in accordance with CSA B52, EPS1/RA/1 and ASME B31.5.

## Brazing Procedures

### Bleed inert gas into pipe during brazing.

### Remove valve internal parts, solenoid valve coils, sight glass.

### Do not apply heat near expansion valve and bulb.

## Piping Installation

### General:

#### Soft annealed copper tubing: bend without crimping or constriction, hard drawn copper tubing: do not bend. Minimize use of fittings.

#### Hot gas lines:

##### Pitch at least 1:240 down in direction of flow to prevent oil return to compressor during operation.

##### Provide trap at base of risers greater than 1800 mm high and at each 6000 mm thereafter.

##### Provide inverted deep trap at top of risers.

##### Provide double risers for compressors having capacity modulation.

###### Large riser: install traps as specified above.

###### Small riser: size for 5.1 m/s at minimum load. Connect upstream of traps on large riser.

## Pressure and Leak Testing

### Close valves on factory charged equipment and other equipment not designed for test pressures.

### Leak test to CSA B52 before evacuation to 2 MPa and 1 MPa on high and low sides respectively.

### Test Procedure: Build pressure up to 35 kPa using nitrogen leave for 8 hours.

## field quality control

### Site Tests/Inspection

#### Close service valves on factory charged equipment.

### Ambient temperatures to be at least 13 degrees C for at least 12 hours before and during dehydration.

### Use copper lines for largest practical size to reduce evacuation time.

### Use two-stage vacuum pump with gas ballast on 2nd stage capable of pulling 5 Pa absolute and filled with dehydrated oil.

### Measure system pressure with vacuum gauge.  Take readings with valve between vacuum pump and system closed.

### Triple evacuate system components containing gases other than correct refrigerant or having lost holding charge as follows:

#### Twice to 14 Pa absolute and hold for 4 h.

#### Break vacuum with refrigerant to 14 KPa.

#### Final to 5 Pa absolute and hold for at least 12 h.

#### Isolate pump from system, record vacuum and time readings until stabilization of vacuum.

#### Submit test results to Owner.

### Charging:

#### Charge system through filter-drier and charging valve on high side.  Low side charging not permitted.

#### With compressors off, charge only amount necessary for proper operation of system.  If system pressures equalize before system in fully charged, close charging valve and start up.  With unit operating, add remainder of charge to system.

#### Re-purge charging line if refrigerant container is changed during charging process.

### Checks:

#### Make checks and measurements as per manufacturer’s operation and maintenance instructions.

#### Record and report measurements to Owner.

### Manufacturer’s Field Services:

#### Have manufacturer of products, supplied under this Section, review work involved in the handling, installation/application, protection and cleaning, of its products and submit written reports, in acceptable format, to verify compliance of work with Contract.

#### Provide manufacturer’s field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer’s instructions.

#### Schedule site visits, to review work, at stages listed:

##### After delivery and storage of products, and when preparatory work, or other work, on which the work of this Section depends, is complete but before installation begins.

##### Twice during progress of work at 25% and 60% complete.

##### Upon completion of the work, after cleaning is carried out.

#### Obtain reports, within three (3) working days of review, and submit, immediately, to Owner.

## demonstration

### Instructions:

#### Post instructions in frame with glass cover in accordance with Section 01 78 00 – Closeout Submittals and CSA B52.

##### Perform cleaning operations as specified in Section 01 74 00 – Cleaning and in accordance with manufacturer’s recommendations.

##### On completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION