# General

## summary

### Section includes:

#### Materials and installation of low-pressure metallic ductwork, joints and accessories.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 07 84 00 – Firestopping

### Section 23 05 29 – Hangers and Supports for HVAC Piping and Equipment.

### Section 23 05 94 – Pressure Testing of Ducted Air Systems.

### Section 23 40 00 – HVAC Air Filtration

## References

### American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc. (ASHRAE).

### American Society for Testing and Materials International, (ASTM).

#### ASTM A 480/A480M, Standard Specification for General Requirements for Flat-Rolled Stainless and Heat-Resisting Steel Plate, Sheet and Strip.

#### ASTM A635/A635M, Standard Specification for Steel, Sheet and Strip, Heavy-Thickness Coils, Hot-Rolled, Alloy, Carbon, Structural, High-Strength Low-Alloy, and High-Strength Low-Alloy with Improved Formability, General Requirements for.

#### ASTM A 653/A653M, Standard Specification for Steel Sheet, Zinc Coated (Galvanized) or Zinc-Iron Alloy Coated (Galvannealed) by the Hot-Dip Process.

### Department of Justice Canada (Jus).

#### Canadian Environmental Protection Act (CEPA).

### Health Canada/Workplace Hazardous Materials Information System (WHMIS).

#### Safety Data Sheets (SDS).

### National Fire Protection Association (NFPA).

#### NFPA 90A, Standard for the Installation of Air-Conditioning and Ventilating Systems.

#### NFPA 90B, Standard for the Installation of Warm Air Heating and Air-Conditioning Systems.

#### NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.

### Sheet Metal and Air Conditioning Contractors' National Association (SMACNA).

#### SMACNA HVAC Duct Construction Standards - Metal and Flexible.

#### SMACNA HVAC Air Duct Leakage Test Manual.

#### IAQ Guideline for Occupied Buildings Under Construction, 1st Edition.

### Transport Canada (TC).

#### Transportation of Dangerous Goods Act (TDGA).

## submittals

### Submit shop drawings and product data in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data: submit WHMIS SDS - Safety Data for the following:

#### Sealants.

#### Tape.

#### Proprietary Joints.

## quality assurance

### Certification of Ratings:

#### Catalogue or published ratings shall be those obtained from tests carried out by manufacturer or independent testing agency signifying adherence to codes and standards.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

#### During construction meet or exceed the requirements of SMACNA IAQ Guideline for Occupied Buildings under Construction.

### Installers to be certified to journeyperson level in sheet metal work.

## delivery, storage and handling

### Protect on site stored or installed absorptive material from moisture damage.

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Separate for reuse and recycling and place in designated containers steel, metal, plastic waste in accordance with Waste Management Plan.

#### Place materials defined as hazardous or toxic in designated containers.

#### Handle and dispose of hazardous materials in accordance with CEPA, TDGA, Regional and Municipal regulations.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

# Products

## Seal Classification

### Classification as follows:

| Maximum Pressure Pa | SMACNA Seal Class |
| --- | --- |
| > 1000 | A |
| 750 | B |
| 500 | C |
| 250 | C |
| 125 | C |

### Seal classification:

#### Class A: longitudinal seams, transverse joints, duct wall penetrations and connections made airtight with sealant and tape.

#### Class B: longitudinal seams, transverse joints and connections made airtight with sealant tape or combination thereof.

#### Class C: transverse joints and connections made air tight with gaskets, sealant tape or combination thereof. Longitudinal seams unsealed.

## Sealant

### Sealant: oil resistant, polymer type flame resistant duct sealant. Temperature range of minus 30°C to plus 93°C.

## Tape

### Tape: polyvinyl treated, open weave fiberglass tape, 50 mm wide.

## Duct Leakage

### In accordance with SMACNA HVAC Duct Leakage Test Manual.

## Fittings

### Fabrication: to SMACNA.

### Radiused elbows:

#### Rectangular: Centreline radius: 1.5 times width of duct.

#### Round: smooth radius or five piece. Centreline radius: 1.5 times diameter.

### Mitred elbows, rectangular:

#### To 400 mm: with single thickness turning vanes.

#### Over 400 mm: with double thickness turning vanes.

### Branches:

#### Rectangular main and branch: with radius on branch 1.5 times width of duct or 450 entry on branch.

#### Round main and branch: enter main duct at 450 with conical connection.

#### Provide volume control damper in branch duct near connection to main duct.

#### Main duct branches: with volume control damper.

### Transitions:

#### Diverging: 200 maximum included angle.

#### Converging: 300 maximum included angle.

### Offsets:

#### Full short radiused elbows as indicated.

### Obstruction deflectors: maintain full cross-sectional area. Maximum included angles: as for transitions.

## Firestopping

### Retaining angles around duct, on both sides of fire separation in accordance with Section 07 84 00 – Firestopping.

### Firestopping material and installation must not distort duct.

## Galvanized Steel

### Lock forming quality: to ASTM A653, G90 zinc coating.

### Thickness, fabrication and reinforcement: to SMACNA.

### Joints: to SMACNA or proprietary manufactured duct joint. Proprietary manufactured flanged duct joint to be considered to be a class A seal.

## Stainless Steel

### To ASTM A480/A480M, Type 304.

### Finish: No 4. finish on exposed side of duct in finished area’s, No. 3 finish or lower where concealed.

### Thickness, fabrication and reinforcement: to SMACNA.

### Joints: to SMACNA and be continuous inert gas welded.

## Aluminum

### To SMACNA. Aluminum type: 3003-H-14.

### Thickness, fabrication and reinforcement: to SMACNA.

### Joints: to SMACNA and be continuous weld.

## Black Steel

### To ASTM A635/A635M.

### Thickness: 1.2 mm

### Fabrication: ducts and fittings or SMACNA.

### Reinforcement: to SMACNA.

### Joints: continuous weld.

## Kitchen Exhaust Systems

### Construct in accordance with NFPA 96.

### Material: Type 304 stainless steel where exposed, stainless steel where concealed or black sheet where concealed.

### Thickness: to NFPA 96.

### Fabrication: joints, continuous inert gas welded for stainless steel, ARC welded for black steel.

### Reinforcement: to SMACNA.

### Drainage: at low point.

### Grease filters: to Section 23 40 00 – HVAC Air Filtration.

## Hangers and Supports

### Strap hangers: of same material as duct but next sheet metal thickness heavier than duct. Maximum size duct supported by strap hanger: 500 mm.

### Hanger configuration: to SMACNA.

### Hangers:  galvanized steel angle with black steel rods to ASHRAE or SMACNA following table:

| Duct Size | Angle Size | Rod Size |
| --- | --- | --- |
| (mm) | (mm) | (mm) |
| up to 750 | 25x25x3 | 6 |
| 751 to 1050 | 40x40x3 | 6 |
| 1051 to 1500 | 40x40x3 | 10 |
| 1501 to 2100 | 50x50x3 | 10 |
| 2101 to 2400 | 50x50x5 | 10 |
| 2401 and over | 50 x 50 x 6 | 10 |

### Upper hanger attachments:

#### For concrete: manufactured concrete inserts.

#### For steel joist: manufactured joist clamp steel plate washer.

#### For steel beams: manufactured beam clamps:

# Execution

## General

### Do work in accordance with NFPA 90A, NFPA 90B, and SMACNA.

### Do not break continuity of insulation vapour barrier with hangers or rods. Insulate strap hangers 100 mm beyond insulated duct.

### Support risers in accordance with SMACNA.

### Install breakaway joints in ductwork on sides of fire separation. Do not place fire stopping material in expansion space between damper sleeve and fire partition.

### Install proprietary manufactured flanged duct joints in accordance with manufacturer's instructions.

### Manufacture duct in lengths and diameter to accommodate installation of acoustic duct lining.

## Hangers

### Strap hangers: install in accordance with SMACNA.

### Angle hangers: complete with locking nuts and washers.

### Hanger spacing: in accordance with SMACNA or as follows:

| Duct Size | Spacing |
| --- | --- |
| (mm) | (mm) |
| to 1500 | 3000 |
| 1501 and over | 2500 |

## Watertight Duct

### Provide watertight duct for:

#### Dishwasher exhaust.

#### Fresh air intake.

#### Minimum 3000 mm from duct mounted humidifier in all directions.

#### As indicated.

### Form bottom of horizontal duct without longitudinal seams. Solder or weld joints of bottom and side sheets. Seal other joints with duct sealer.

### Slope horizontal branch ductwork down towards fume hoods served. Slope header ducts down toward risers.

### Fit base of riser with 150 mm deep drain sump and NPS 1 ½ drain connected, with deep seal trap and valve and discharging to open funnel drain or service sink or as approved by Owner.

## Kitchen Exhaust Systems

### Install to NFPA 96 and as indicated.

## Sealing and Taping

### Apply sealant to outside of joint to manufacturer's recommendations.

### Bed tape in sealant and recoat with minimum of one coat of sealant to manufacturers recommendations. Sealant and tape to be applied to full perimeter of duct.

## Leakage Tests/COMMISSIOONING

### Refer to Section 23 05 94 - Pressure Testing of Ducted Air Systems.

### In accordance with SMACNA HVAC Duct Leakage Test Manual.

### Do leakage tests in sections.

### Make trial leakage tests as instructed to demonstrate workmanship.

### Install no additional ductwork until trial test has been passed.

### Test section minimum of 30 m long with not less then three branch takeoffs and two 90º elbows.

### Complete test before insulation or concealment.

END OF SECTION