# General

## SUMMARY

### Section Includes:

#### Materials and installation for duct accessories including flexible connections, access doors, vanes and collars.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

## REFERENCES

### Health Canada/Workplace Hazardous Materials Information System (WHMIS).

#### Safety Data Sheets (SDS).

### Sheet Metal and Air Conditioning Contractors’ National Association (SMACNA).

#### SMACNA – HVAC Duct Construction Standards – Metal and Flexible.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Product Data:

#### Submit manufacturer’s printed product literature, specifications and data sheet.  Indicate the following:

##### Flexible connections

##### Duct access doors.

##### Turning vanes.

##### Instrument test ports.

#### Submit WHMIS SDS in accordance with Section 01 33 00 - Submittal Procedures.  Indicate VOC’s for adhesive and solvents during application and curing.

### Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

#### Certification of ratings: catalogue or published ratings to be those obtained from tests carried out by manufacturer or independent testing agency signifying adherence to codes and standards.

### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions: submit manufacturer’s installation instructions.

### Manufacturer’s Field Reports: manufacturer’s field reports specified.

### Closeout Submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## QUALITY ASSURANCE

### Pre-Installation Meetings:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation and substrate conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer’s installation instructions and warranty requirements.

#### Health and Safety:

##### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal paper, plastic, polystyrene, and corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers steel, metal, and plastic waste in accordance with Waste Management Plan (WMP).

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

# Products

## General

### Manufacture in accordance with SMACNA - HVAC Duct Construction Standards.

## Flexible Connections

### Frame: galvanized sheet metal frame 0.66 mm thick with fabric clenched by means of double locked seams.

### Material:

#### Fire resistant, self extinguishing, neoprene coated glass fabric, temperature rated at minus 400C to plus 900C, density of 1.3 kg/m2.

## Access Doors in Ducts

### Non-insulated ducts: sandwich construction of same material as duct, one sheet metal thickness heavier, minimum 0.6 mm thick complete with sheet metal angle frame.

### Insulated ducts: sandwich construction of same material as duct, one sheet metal thickness heavier, minimum 0.6 mm thick complete with sheet metal angle frame and 25 mm thick rigid glass fibre insulation.

### Gaskets: neoprene.

### Hardware:

#### Hold open devices.

#### 300 x 300 mm glass viewing panels.

#### Up to 300 x 300 mm: two sash locks complete with safety chain.

#### 301 to 450 mm: four sash locks complete with safety chain.

#### 451 to 1000 mm: piano hinge and minimum two sash locks.

#### Doors over 1000 mm: piano hinge and two handles operable from both sides.

##### Hold open devices.

##### 300 X 300 mm glass viewing panels.

## Turning Vanes

### Factory or shop fabricated double thickness with trailing edge, to recommendations of SMACNA and as indicated.

## Instrument Test PORTS

### 1.6 mm thick steel zinc plated after manufacture.

### Cam lock handles with neoprene expansion plug and handle chain.

### 28 mm minimum inside diameter. Length to suit insulation thickness.

### Neoprene mounting gasket.

## Spin-In Collars

### Conical galvanized sheet metal spin-in collars with lockable butterfly damper.

### Sheet metal thickness to co-responding round duct standards.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Flexible connections:

#### Install in following locations:

##### Inlets and outlets to supply air units and fans.

##### Inlets and outlets of exhaust and return air fans.

##### As indicated.

#### Length of connection: 100 mm.

#### Minimum distance between metal parts when system in operation: 75 mm.

#### Install in accordance with recommendations of SMACNA.

#### When fan is running:

##### Ducting on sides of flexible connection to be in alignment.

##### Ensure slack material in flexible connection.

### Access doors and viewing panels:

#### Size:

##### 600 x 600 mm for person size entry.

##### 450 x 450 mm for servicing entry.

##### 300 x 300 mm for viewing.

##### As indicated.

#### Locations:

##### Fire and smoke dampers.

##### Control dampers.

##### Devices requiring maintenance.

##### Required by code.

##### Reheat coils.

##### Elsewhere as indicated.

### Instrument test ports.

#### General:

##### Install in accordance with recommendations of SMACNA and in accordance with manufacturer's instructions.

#### Locate to permit easy manipulation of instruments.

#### Install insulation port extensions as required.

#### Locations.

##### For traverse readings:

###### Ducted inlets to roof and wall exhausters.

###### Inlets and outlets of other fan systems.

###### Main and sub-main ducts.

###### And as indicated.

##### For temperature readings:

###### At outside air intakes.

###### In mixed air applications in locations as approved by Owner.

###### At inlet and outlet of coils.

###### Downstream of junctions of two converging air streams of different temperatures.

###### And as indicated.

### Turning vanes:

#### Install in accordance with recommendations of SMACNA and as indicated.

## FIELD QUALITY CONTROL

### Manufacturer’s Field Services:

#### Have manufacturer’s representative of products, supplied under this Section, review Work involved in the handling, installation/application, protection and cleaning, of its products and submit written reports, in acceptable format, to verify compliance of Work with Contract.

#### Manufacturer’s Field Services: provide manufacturer’s field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer’s instructions.

#### Schedule site visits, to review Work, at stages listed:

##### After delivery and storage of products, and when preparatory Work, or other Work, on which the Work of this Section depends, is complete but before installation begins.

##### Twice during progress of Work at 25% and 60% complete.

##### Upon completion of the Work, after cleaning is carried out.

#### Obtain reports, within three (3) working days of review, and submit, immediately, to Owner.

## CLEANING

### Perform cleaning operations as specified in Section 01 74 00 – Cleaning and in accordance with Manufacturer’s recommendations.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION