# General

## summary

### Section Includes:

#### Operating dampers for mechanical forced air ventilation and air conditioning systems.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

## References

### American Society for Testing and Materials International (ASTM)

#### ASTM A 653/A653M-04a, Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by Hot-Dip Process.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

#### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

#### Indicate the following:

##### Performance data.

##### Specifications

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals:

#### Provide maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals

## quality assurance

### Health and Safety Requirements:  Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

### Certificates:

#### Catalogue or published ratings those obtained from tests carried out by manufacturer or those ordered by manufacturer from independent testing agency.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer’s written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Multi-Leaf Dampers

### Opposed or parallel blade type as indicated.

### Structurally formed steel or extruded aluminum, interlocking blades, complete with extruded vinyl seals, spring stainless steel side seals, structurally formed and welded galvanized steel or extruded aluminum frame.

### Pressure fit self-lubricated bronze bearings.

### Linkage: plated steel tie rods, brass pivots and plated steel brackets, complete with plated steel control rod.

### Operator: to Section 25 30 02 – EMCS:  Field Control Devices.

### Performance:

#### Leakage: in closed position to be less than 2% of rated air flow at 500 Pa differential across damper.

#### Pressure drop: at full open position to be less than 25 Pa differential across damper at 10 m/s.

### Insulated aluminum dampers:

#### Frames: insulated with extruded polystyrene foam with RSI factor of 5.0.

#### Blades: constructed from aluminum extrusions with internal hollows insulated with polyurethane or polystyrene foam, RSI factor of 5.0.

## Disc Type Dampers

### Frame: insulated brake formed, welded, 1.6 mm thick, galvanized steel to ASTM A 653M.

### Disc: insulated spin formed, 1.6 mm thick, galvanized steel to ASTM A 653M.

### Gasket: extruded neoprene, field replaceable, with 10 year warranty.

### Bearings: roller self lubricated and sealed.

### Operator: compatible with damper, linear stroke operator, spring loaded actuator, zinc-aluminum foundry alloy casting cam follower.

### Performance:

#### Leakage: in closed position to be less than 2 % of rated air flow at 500 Pa pressure differential across damper.

#### Pressure drop: at full open position to be less than 25 Pa differential across damper at 10 m/s.

## Back Draft Dampers

### Automatic gravity operated, multi leaf, aluminum or steel construction with nylon bearings, centre pivoted, spring assisted or counterweighted.

## Relief Dampers

### Automatic multi-leaf steel or aluminum dampers with ball bearing centre pivoted and counter-weights set to open as indicated.

# Execution

## Installation

### Install where indicated.

### Install in accordance with recommendations of SMACNA and manufacturer's instructions.

### Seal multiple damper modules with silicon sealant.

### Install access door adjacent to each damper. See Section 23 33 00 – Air Duct Accessories.

### Ensure dampers are observable and accessible.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION