# General

## SUMMARY

### Section Includes:

#### Fans, window ventilators, exterior, wall and ceiling mounted discharge fans for domestic use.

## Related Sections

### Section 01 33 00 – Submittal Procedures

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals

### Section 23 05 13 – Common Motor Requirements for HVAC Equipment.

### Section 23 05 48 – Vibration and Seismic Controls for HVAC Piping and Equipment.

### Section 23 33 00 – Air Duct Accessories.

## REFERENCES

### American National Standards Institute/Air Movement and Control Association (ANSI/AMCA)

#### ANSI/AMCA 201, Fans and Systems.

#### ANSI/AMCA Standard 300, Reverberant Room Method for Sound Testing of Fans.

#### ANSI/AMCA Standard 301, Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

#### ANSI/ AMCA 302, Application of Sone Ratings for Non-Ducted Air Moving Devices.

#### ANSI/ AMCA 303, Application of Sound Power Level Ratings for Fans.

### American National Standards Institute (ANSI)/American Society of Mechanical Engineers (ASME)

#### ANSI/AMCA 210, Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

## SYSTEM DESCRIPTION

### Performance Requirements:

#### Catalogued or published ratings for manufactured items: obtained from tests carried out by manufacturer or those ordered by manufacturer from independent testing agency signifying adherence to codes and standards in force.

## SUBMITTALS

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures

#### Indicate following:  dimensions, performance, sound rating, and installation procedure.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals

#### Provide maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## MAINTENANCE

### Extra Materials:

#### Provide maintenance materials in accordance with Section 01 78 00 - Closeout Submittals.

#### Furnish list of individual manufacturer's recommended spare parts for equipment, include:

##### Bearings and seals.

##### Belts

##### Addresses of suppliers.

##### List of specialized tools necessary for adjusting, repairing or replacing.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Fans General

### Standard of rating:

#### AMCA 201 for fan application.

#### AMCA 302 for application of sone loudness ratings for non-ducted air moving devices.

#### AMCA 303 for application of sound power ratings for ducted air moving devices.

#### Performance: to ANSI/AMCA 210 and ANSI/ASHRAE 51.

### Pwl sound ratings to comply with AMCA 301, tested to AMCA 300

### Maximum loudness: 5 sones.

## Exterior Mounted Discharge Fans

### Wall or Roof mounted, direct driven centrifugal fan, ball bearing thermally protected motor.

### Sizes and capacity: see schedule

### Control: switch or thermostatically operated.

### Rust resistant aluminum or zinc coated steel, baked-on enamel finish with aluminum backdraft damper, spring loaded complete with foam cushioned frame.

## Wall and Ceiling DIscharge Fans

### Centrifugal direct drive, with plug-in type electric motor suitable for ceiling or wall installation, zinc coated rectangular metal housing.

### Sizes and capacity: see schedule.

### Toggle switch or timer operated complete with integral electrical outlet box with plug-in type receptacle.

### Top or side 80 mm x 250 mm rectangular duct outlet with integral backdraft damper.

### Roof jack or wall cap complete with spring loaded backdraft damper with neoprene gasket.

### White polymeric or silver anodized aluminum grille.

# Execution

## MANUFACTURER’S instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with manufacturer's recommendations.

## ANchor bolts and templates

### Supply for installation by other divisions.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## COMMISSIONING

### Commission in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION