# General

## summary

### Section Includes:

#### Roof and wall exhausters.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 33 15 – Dampers – Operating.

## REFERENCES

### American Bearing Manufacturers Association (ABMA)

### Air Movement and Control Association (AMCA)

#### AMCA Publication 99, Standards Handbook (Revised 2003).

#### AMCA 300, Reverberant Room Method for Sound Testing of Fans.

#### AMCA 301, Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

### American National Standards Institute (ANSI)

#### ANSI/AMCA 210, Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

## SYSTEM DESCRIPTION

### Performance Requirements:

#### Catalogued or published ratings for manufactured items: obtained from tests carried out by manufacturer or those ordered by manufacturer from independent testing agency signifying adherence to codes and standards in force. Provide confirmation of testing.

#### Capacity: flow rate, total static pressure Pa, r/min, bhp W, model and size and sound ratings as indicated on schedule.

### Statically and dynamically balanced. Constructed to AMCA 99.

### Sound ratings: comply with AMCA 301, tested to AMCA 300. Unit shall bear AMCA certified sound rating seal.

### Performance ratings: based on tests performed in accordance with ANSI/AMCA 210, unit to bear AMCA certified rating seal.

### Bearings: sealed lifetime oilite ball bearings, heavy duty grease lubricated ball or roller bearings of self aligning type with oil retaining, dust excluding seals and a certified minimum rated L10 life of 100,000 hours.

## SUBMITTALS

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

#### Include:

##### Fan performance curves showing specified point of operation.

##### Sound rating data.

##### Installation procedures.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals

#### Provide operation and maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06- Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

## MAINTENANCE

### Extra Materials:

#### Provide maintenance materials in accordance with Section 01 78 00 - Closeout Submittals.

### Furnish list of individual manufacturer's recommended spare parts for equipment, include:

#### Bearings and seals.

#### Belts.

#### Addresses of suppliers.

#### List of specialized tools necessary for adjusting, repairing or replacing.

# Products

## Fans General

### Capacity: flow rate, static pressure Pa, r/min, bhp, model and size and sound ratings as indicated on schedule.

### Statically and dynamically balanced. Constructed in conformity with AMCA 99.

### Sound ratings: comply with AMCA 301, tested to AMCA 300.

### Performance ratings: based on tests performed in accordance with ANSI/ASHRAE 51/AMCA 210.

### Bearings: sealed lifetime ball bearings or heavy duty grease lubricated ball or roller bearings of self aligning type with oil retaining, dust excluding seals and a certified minimum rated life to ABMA L10 of 100,000 h.

## Roof Exhausters

### Centrifugal V belt or direct driven.

#### Housings: spun aluminum complete with resilient mounted motor and fan.

#### Impeller: aluminum non-overloading.

#### Adjustable motor sheave.

#### 12 mm mesh 2.0 mm dia aluminum birdscreen.

#### Motorized gasketted insulated aluminum back draft dampers to Section 23 33 15 – Dampers – Operating.

#### Weatherproof disconnect switch within fan housing.

#### Roof curb, 350 mm high, continuous curb gaskets, cadmium plated or stainless steel securing bolts and screws, and special mated sound insulating 350 mm high curbs where indicated. Hinge curb plate for access to internals for maintenance.

### Eisenheiss coated wheel and upblast discharge for fume hood service with motor out of air stream.

### Sound curbs: of same manufacturer as fan and built to suit model specified.

#### Double baffle and self-flashing type. Required decibel sound attenuation spectrum:

| Frequency Octave Band | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| dB Attenuation | 3 | 5 | 11 | 16 | 22 | 20 | 17 | 13 |

#### Pressure loss through curbs: 37 Pa max at rated L/s.

### Two speed fan motors: two windings or split windings with speeds of approximately 1800 RPM high and 900 RPM.

## Wall Exhausters

### Centrifugal backward inclined fan units, V belt or direct driven.

#### Spun aluminum housings, complete with resilient mounted motor and fan.

#### 12 mm mesh 2.0 mm dia aluminum birdscreen.

#### Motorized gasketted insulation aluminum back draft dampers to Section 23 33 15 – Dampers - Operating.

#### Weatherproof disconnect switch within fan housing.

#### Cadmium plated or stainless steel securing bolts and screws.

### Housings:

#### Provide with rubber or neoprene grommets for wiring passages, integral attachment collar, or angle ring mounted to mating flanged wall sleeve with full gasketting.

#### Discharge pattern: away from building.

### Two speed motors: two windings or with speeds of approximately 1800 r/min high and 900 r/min low as indicated.

## Roof Exhausters for Grease Exhaust

### Entire fan housing, cowl and discharge 16 gauge cold rolled steel, continuously welded and liquid tight to NFPA 96 requirements.

### Unit complete with 1.6 mm pitched where indicated, roof curb, cold rolled steel shipped separately for field installation, discharger clearance 1000 mm above roof.

### The exhaust duct collar 25 mm insulated double skin, 1.6 mm inner skin, 0.9 mm outer skin, cold rolled steel, all welded.  Extend 305 mm minimum below the roof line and have a 38 mm flanged connection for welding or bolting to the duct system.  Minimum clearance from duct collar to combustible roof opening 74 mm as per U.L.C. approvals.

### The fan wheel all welded, statically and dynamically balanced at factory, with single inlet and backward inclined blades to provide non-overloading characteristics and minimum noise level.  Bearings grease lubricated, heavy duty self-aligning flange type, mounted outside of air steam on oversized, polished steel shaft.

### Unit complete with smoothly curved inlet venturi, to create a stream-lined air flow into the fan wheel.

### Complete unit factory primed and painted, ready for outside installation.

### Fan to have electrical disconnect switch, supplied wired to the fan motor and an electrical conduit sleeve that runs the complete length of the duct collar.  High temperature wire provided in conduit to point approximately 152 mm below the duct collar.

### Adjustable pitch (1 or 2 groove) pulleys provided factory set at proper operating speed from motors up to the 5 H.P., fixed pulleys provided over 5 HP.

### Fan Underwriter Laboratories approved as a power roof ventilator for kitchen exhaust systems

### Complete with gravity back draft damper located at the fan discharge.

# EXECUTION

## MANUFACTURER’S instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with manufacturer's instructions.

### Install fans for grease exhaust fans in accordance with NFPA 96.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## COMMISSIONING

### Commissioning in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION