# General

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 45 00 – Quality Control.

### Section 01 74 21 – Construction/Demolition Waste Submittal and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 32 48 – Acoustical Air Plenums.

## References

### American National Standards Institute (ANSI)

#### ANSI/AMCA 210, Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

#### ANSI/NFPA 90A, Standard for the Installation of Air Conditioning and Ventilating Systems.

### American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE)

#### AHSRAE 130, Methods of Testing for Rating Ducted Air Terminal Units.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

### International Organization of Standardization (ISO)

#### ISO 3741, Acoustics-Determination of Sound Power Levels of Noise Sources Using Sound Pressure - Precision Methods for Reverberation Rooms.

### Underwriter's Laboratories (UL)

#### UL 181, Factory-Made Air Ducts and Air Connectors.

## SYSTEM DESCRIPTION

### Performance Requirements:

#### Catalogued or published ratings for manufactured items: obtained from tests carried out by manufacturer or those ordered by manufacturer from certified ADC (Air Diffusion Council) testing agency signifying adherence to codes and standards.

## SUBMITTALS

### Product Data:

#### Submit manufacturer’s printed product literature, specifications and datasheet in accordance with Section 01 33 00 –Submittal Procedures.  Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 – Submittal Procedures.

#### Test data: to ANSI/AMCA 210.

##### Submit published test data on DIN (Direct Internal Noise), in accordance with ISO 3741 made by independent testing agency for 0, 2.5 and 6 m/s branch velocity or inlet velocity.

##### Sound power level with minimum inlet pressure of 0.25, 0.5, 1, and 1.5 kPa in accordance with ISO 3741 for 2nd through 7th octave band, also made by independent testing agency.

##### Pressure loss through silencer shall not exceed 60% of inlet velocity pressure maximum.

### Shop Drawings:

#### Submit shop drawing in accordance with Section 01 33 00 – Submittal Procedures.

#### Indicate the following:

##### Capacity.

##### Pressure drop.

##### Noise rating.

##### Leakage.

##### Dimensions.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 – Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer’s installation instructions.

### Closeout Submittals:

#### Provide maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver store and handle in accordance with Section 01 61 00 – Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer’s written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

## MAINTENANCE

### Extra Materials:

#### Provide maintenance materials in accordance with Section 01 78 00 – Closeout Submittals.

#### Furnish list of individual manufacturer’s recommended spare parts for equipment.  Include:

##### Bearings and seals.

##### Addresses of suppliers.

##### List of specialized tools necessary for adjusting, repairing or replacing.

# Products

## Manufactured Units

### Terminal units of the same type to be product of one manufacturer.

## Variable Volume Boxes

### Pressure independent factory reset to air flow between minimum and maximum air volume.

### Sizes, capacities, differential pressures and sound ratings: as indicated in schedule.

### Differential pressure not to exceed 25 Pa at inlet air velocity of 10 m/s.

### Sound ratings of assembly not to exceed 35 NC at 750 Pa. Use sound attenuator if necessary to achieve rating.

### Complete with:

#### Operator and controller: as specified under Section 25 30 02 – EMCS:  Field Control Devices.

#### Sound attenuator: as indicated or as specified in Section 23 32 48 – Acoustical Air Plenums.

#### Multiport outlet adapter: as indicated.

#### Reheat coil: as indicated.

### Minimum 35 kPa reset span for pneumatic controllers.

### Adjustable reset start point.

### Operator to be factory or field mounted and calibrated where indicated.

#### Gauge taps for balancing with standard pressure gauge.

#### Controller to have adjustable flow settings.

### Casing: constructed of 0.75 mm thick galvanized steel, internally lined with 25 mm, 0.7 kg density fibrous glass, to UL181 and ANSI/NFPA 90A. Mount control components inside protective metal shroud.

### Damper: galvanized steel with peripheral gasket and self lubricating bearings. Air leakage past closed damper not to exceed 2% of nominal rating at 750 Pa inlet static pressure, in accordance with Air Diffusion Council test procedure.

## Constant Volume Bypass Boxes

### Maintains space condition by bypassing supply air to return air.

### Sizes, capacities, pressure loss, and discharge sound pressure level: as indicated.

### Discharge sound pressure level: to be less than 35 NC.

### Complete with:

#### Bypass collar for connection to return air duct.

#### Minimum air volume stop.

#### Controller and operator as specified under 25 30 02 –EMCS:  Field Control Devices.

#### Reheat coil as indicated.

#### Manual balancing damper.

#### Multi-port outlets.

#### Sound attenuator: as indicated.

### Casing: constructed of 0.75 mm thick galvanized steel, internally lined with 25 mm, 0.7 kg density fibrous glass, to UL 181 and ANSI/NFPA 90A. Mount control components inside protective metal shroud.

### Damper: galvanized steel with peripheral gasket and self lubricating bearings. Air leakage past closed damper not to exceed 2% of nominal rating at 750 Pa inlet static pressure, in accordance with Air Diffusion Council test procedure.

### Sequence of operation as specified under Section 25 90 01 – EMCS:  Site Requirements, Applications and Systems Sequence of Operations.

## Fan Powered Boxes

### General:

#### Primary air assembly, pressure independent with reset to any air flow between minimum and maximum air volume as indicated.

#### Sound ratings of assembly not to exceed 35 NC at 750 Pa. on discharge.

#### Field calibration and readjustment of air volume to be as follows:

##### Gauge tops for balancing with standard pressure gauge and

##### Adjustable flow settings.

#### Casing: constructed of heavy gauge, galvanized steel, internally lined with 25 mm, 0.7 kg density fibrous glass, to UL181 and ANSI/NFPA 90A. Mount control components inside protective metal shroud.

#### Damper:  galvanized steel with peripheral gasket and self lubricating bearings. Air leakage past closed damper not to exceed 2% of nominal rating at 750 Pa inlet static pressure, in accordance with Air Diffusion Council test procedure.

#### Complete with:

##### Sound attenuator: as indicated

##### Reheat coil as indicated.

##### Multiport outlet adapter: as indicated.

### Fan section.

#### CSA certified.

#### Forward curved, centrifugal, direct drive, permanently lubricated motor, internally suspended and isolated from casing on rubber-in-shear isolators complete with access panel.

#### Fan controls to be sealed from primary air flow.

#### Electrical characteristics: 120/1/60.

### Sequence of operation as specified under Section 25 90 01 – EMCS:  Site Requirements, Applications and Systems Sequence of Operations.

# Execution

## MANUFACTURER’S instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with manufacturers recommendations.

### Support independently of ductwork.

### Install with at least 1000 mm of rigid inlet ducting and minimum of four duct diameters of straight inlet duct, same size as inlet.

### Locate so that controls, dampers and access panels are easily accessible.

## CLEANING

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## COMMISSIONING

### Commission in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION