# General

## SUMMARY

### Section Includes:

#### Mechanical louvers; intakes; vents; and reinforcement and bracing for air vents, intakes and gooseneck hoods.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

## REFERENCES

### Air Movement and Control Association (AMCA)

#### AMCA 540, Test Method for Louvres Impacted by Wind Borne Debris.

#### AMCA 550, Test Method for High Velocity Wind Driven Rain Resistant Louvres.

### American National Standards Institute (ANSI)/ National Fire Protection Association (NFPA)

#### ANSI/NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.

### American Society for Testing and Materials International (ASTM)

#### ASTM E 90, Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

### Sheet Metal and Air Conditioning Contractors' National Association (SMACNA)

### Society of Automotive Engineers (SAE)

## SYSTEM DESCRIPTION

### Performance Requirements:

#### Catalogued or published ratings for manufactured items: obtained from tests carried out by manufacturer or those ordered by manufacturer from independent testing agency signifying adherence to codes and standards.

## SUBMITTALS

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

##### Indicate following:

###### Pressure drop.

###### Face area.

###### Free area.

###### Dimensions

#### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

##### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

##### Instructions: submit manufacturer's installation instructions.

#### Test Reports:

##### Submit certified data from independent laboratory substantiating acoustic and aerodynamic performance to ASTM E 90.

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

#### Deliver, store and handle materials in accordance with manufacturer's written instructions.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Gravity Roof Outside Air Intakes and Relief Vents

### Factory manufactured aluminum hinged at curb line.

#### Complete with integral birdscreen of 2.7 mm diam 12 mm mesh aluminum wire.

#### Vertical or horizontal backdraft dampers on four faces.

#### Maximum throat velocity: 3.3 m/s intake.

#### Maximum loss through unit: 15 Pa exhaust static pressure.

#### Maximum velocity through damper area: 1.5 m/s.

#### Shape: as indicated.

## Gooseneck Hoods

### Thickness: to SMACNA.

#### Kitchen: to ANSI/NFPA 96.

#### Elsewhere: to SMACNA.

### Fabrication: to SMACNA.

#### Kitchen: to ANSI/NFPA 96.

#### Elsewhere: to SMACNA.

### Joints: to SMACNA or proprietary manufactured duct joint. Proprietary manufactured flanged duct joint shall be considered to be a class A seal.

### Supports: as indicated.

### Complete with integral birdscreen of 2.7 mm diameter aluminum wire. Use 12 mm mesh on exhaust and intake.

### Horizontal backdraft dampers.

## Fixed Louvres - Aluminum

### Construction: welded with exposed joints ground flush and smooth.

### Material: extruded aluminum alloy 6063-T5.

### Blade: drainable, stormproof pattern with centre watershed in blade, reinforcing bosses and maximum blade length of 1500 mm.

### Frame, head, sill and jamb: 100 mm deep one piece extruded aluminum, minimum 3 mm thick with approved caulking slot, integral to unit. Flanged frame or flush frame as indicated.

### Mullions: at 1500 mm maximum centres.

### Fastenings: stainless steel with nuts and resilient neoprene washers between aluminum and head of bolt, or between nut, ss washer and aluminum body.

### Screen: 12 mm on exhaust and intake mesh, 2.0 mm diameter wire aluminum or galvanized birdscreen on inside face of louvres in formed U-frame.

### Finish: factory applied enamel, or anodized as indicated. Colour: to Owner’s approval.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### In accordance with manufacturer's and SMACNA recommendations.

### Reinforce and brace as indicated.

### Anchor securely into opening. Seal with caulking around to ensure weather tightness.

## Cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION