# General

## summary

### Section includes:

#### Materials, accessories, and installation for breeching, chimney’s, and stacks.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 01 78 00 - Closeout Submittals.

### Section 03 30 00 - Cast-in-Place Concrete.

## References

### Sheet Metal and Air Conditioning Contractors National Association (SMACNA)

### Underwriters' Laboratories of Canada (ULC)

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS)

## submittals

### Product Data

#### Submit manufacturer’s printed product literature, specifications and datasheet in accordance with Section 01 33 00 – Submittal Procedures.  Include product characteristics, performance criteria, and limitations.

#### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 – Submittal Procedures.

### Shop Drawings

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

#### Indicate following:

##### Methods of sealing sections.

##### Methods of expansion.

##### Details of thimbles.

##### Bases/Foundations.

##### Supports.

##### Guy details.

##### Rain caps.

##### Installation procedures.

### Quality assurance submittals:  submit following in accordance with Section 01 33 00 – Submittal Procedures.

#### Certificates:  submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Closeout Submittals

#### Submit operation and maintenance data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.

## quality assurance

### Regulatory Requirements:  work to be performed in compliance with Canadian Environmental Protection Act (CEPA), Canadian Environmental Assessment Act (CEAA), Transportation of Dangerous Goods Act (TDGA), and applicable Provincial regulations.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 – Health and Safety Requirements.

### Certificates:

#### Catalogued or published ratings:  obtained from tests carried out by independent testing agency or manufacturer signifying adherence to codes and standards.

## Delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Breeching

### Shop fabricated 3.5 mm thick mild steel, or stainless welded, with sweep bends from boiler outlet to thimble or chimney as indicated per 2.2 below.

## Fuels: Pressure Chimney and Breeching

### ULC labelled, 760oC rated, all fuels.

### Sectional, prefabricated, double wall with air space and mineral wool insulation with mated fittings and couplings.

#### Liner: 0.9 mm thick, type 304 stainless steel up to 900 mm diameter, 1.2 mm up to 1200 mm.

#### Shell: 0.6 mm thick, type 304 stainless steel up to 600 mm diameter, 0.9 mm up to 1200 mm.

#### Outer seals between sections: to suit application.

#### Inner seals between sections: to suit application.

#### Insulation thickness:  25 mm minimum, location in Labrador 50 mm minimum.

#### Guy section and guy tensions where indicated.

#### Storm collar and flashing for non-combustible roofs.

#### Ventilated roof thimble and roof support assembly for combustible roofs.

#### Stack cap.

#### Lateral tee 45o, drain tee cap.

## Steel Chimney Refractory Lined (OVer 1200 mm diameter)

### Material:

#### Prefabricated sections with 90 mm thick high temperature impervious insulating refractory lining, centrifugally spun into 3.5 mm thick circular casing.

### Construction:

#### Prefabricated sections, welded on site or at factory. Use high temperature insulating cement at joints in refractory lining.

### Welding:

#### To full thickness. All welds ground smooth.

### Supports:

#### Welded gussets, cleats and bolts for installation on concrete base.

#### Chimney to be self supporting or laterally and vertically braced.

#### Concrete base by Section 03 30 00- Cast-in-Place Concrete.

### Breeching entry:

#### Tee section with 150 mm minimum refractory lined projection.

### Access door, in bottom section.

### Drain connection, at base of stack.

### Dimensions, as indicated.

## Accessories

### Cleanouts: bolted, gasketted type, full size of breeching, as indicated.

### Barometric dampers: single or double acting, 70% of full size of breeching area, as recommended by manufacturer.

### Hangers and supports: in accordance with recommendations of Sheet Metal and Air Conditioning Contractors National Association Inc. (SMACNA).

### Rain cap.

### Expansion sleeves with heat resistant caulking, held in place as indicated.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation - General

### Follow manufacturer's and SMACNA installation recommendations for shop fabricated components.

### Suspend breeching at 1.5 m centres and at each joint.

### Support chimneys at bottom, roof and intermediate levels as indicated.

### Install thimbles where penetrating roof, floor, ceiling and where breeching enters masonry chimney. Pack annular space with heat resistant caulking.

### Install flashings on chimneys penetrating roofs, as indicated.

### Install rain caps and cleanouts, as indicated.

## INSTALLATION - REFRACTORY LINED STEEL CHIMNEY

### Grind all welds smooth to form appearance of single tube.

### Seal insulating refractory at top of stack.

### Pack annular space around breeching at entry tee with heat resistant caulking.

### Run drain line from drain connection to nearest floor drain or ground.

### On completion, paint one coat of rust inhibitive primer and two coats of heat resisting paint of colour, make and quality as approved by Owner.

## cleaning

### Proceed in accordance with Section 01 74 00 – Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION