# General

## RELATED WORK

### The contractor is to ensure that all related work is coordinated among all specification sections and that the tender price includes all related work.  The referenced sections below are for guidance only and are not necessarily a complete list of related sections.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 03 30 00 – Cast-in-Place Concrete

### Section 23 84 13 - Humidifiers.

## REFERENCES

### American National Standards Institute (ANSI)

#### ANSI Z21.64, Direct Vent Central Furnaces.

### American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE)

#### ASHRAE 52.1, Gravimetric and Dust Spot Procedures for Testing Air-Borne Cleaning Devices Used in General Ventilation for Removing Particulate Matter.

### Canadian Standards Association (CSA International)

#### CAN/CSA-B139, Installation Code for Oil Burning Equipment.

#### CSA B140.2.2, Pressure Atomizing Oil Burner Nozzles.

#### CSA B140.4, Oil-Fired Warm Air Furnaces.

#### CSA B140.14, Automatic Flue-Pipe Dampers for Use with Oil Fired Appliances.

#### CAN/CSA-B140.2.1, Oil Burners, Atomizing Type.

#### CSA C22.1 Canadian Electrical Code.

#### CSA C22.2 No.24, Temperature-Indicating and Regulating Equipment.

#### CSA C22.2 No.46, Electric Air-Heaters.

## SHOP DRAWINGS

### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Include following: installation instructions, capacity, dimensions, weights, wiring diagrams.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

### Include following: shop drawings, operation and maintenance manual.

## waste management and disposal

### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal, and with the Waste Reduction Workplan.

### Remove from site and dispose of all packaging materials at appropriate recycling facilities.

### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility as approved by Engineer.

## EXTRA MATERIALS

### Spare filters: in addition to filters installed immediately prior to acceptance by Owner, supply 1 complete set of filters for each filter unit or filter bank in accordance with section 01 78 00 - Closeout Submittals.

# Products

## GENERAL

### Provide CSA  approved, packaged factory assembled unit consisting of cabinet, fan, fan motor, intake/exhaust assembly, heat exchanger, combustion chamber, burner, controls, air filter, condensate drain, and humidifier to Section 23 84 13 - Humidifiers.

### Mid efficiency level range: 80%.

### Certification of components and construction of factory assembled oil-fired unit: to CSA B140.4.

## CAPACITY

### Output: as indicated.

### Air flow rate: as indicated.

### External static pressure: as indicated.

### Input: as indicated.

### Electrical characteristics: as indicated.

## TYPE

### Upflow, Downflow/Counterflow, Horizontal, Low boy type with oil burner.

## CABINET

### 1.0 mm thick minimum steel with baked enamel finish.

### Welded steel base for floor type.

### Easily removed and secured access doors for components requiring service.

### Thermally insulated cabinet with minimum 25 mm thick insulation.

### Cabinet to be equipped with brackets for floor mounting or ceiling hung. Provide rubber-in-shear or spring mounted isolators to Section 23 05 48 – Vibration and Seismic Controls for HVAC Piping and Equipment.

## HEAT EXCHANGER

### Primary: stainless steel tube type 430 with stainless steel fins.

### Secondary:  stainless steel tube with stainless steel fins.

### Warranty: 3 years.

## COMBUSTION CHAMBER

### Power vent, forced draft: to manufacturer’s standard.

### Exhaust stack direct drive induced draft fan.

## CIRCULATION BLOWER MOTOR ASSEMBLY

### Blower: centrifugal type:

#### Statically and dynamically balanced.

#### Rubber mounted.

#### Speed adjustment: adjustable V-belt shieve.

### Motor: as indicated, Hz, 1750 r/min. single speed, overload protection, adjustable mounts.

## AIR FILTERS

### 25 mm thick, glass fiber, disposable type 35 % efficiency to ASHRAE 52.

## HUMIDIFIERS

### To Section 23 84 13 - Humidifiers.

## HEATER BURNER

### General: to bear CSA and ULC labels.

### Oil burner:

#### High pressure atomizing type, certified to CAN/CSA B140.2.1.

#### Pressure atomizing oil burner nozzle, certified to CSA B140.2.2 and flame retention head.

#### Two stage fuel pump.

#### Burner shall be equipped for controlled modulated firing, including modulating damper motor, proportioning air damper, fuel metering valves, end switch, solenoid valves and necessary linkage to assure proper air/fuel ratio at all firing rates.  The burner shall be factory tested and adjusted for a high/low fire turndown ratio of 10 to 1.

## INTAKE AND VENT ASSEMBLY

#### To Section 23 51 00 – Breeching, Chimneys and Stacks.

#### Provide barometric damper.

## CONTROLS

### General: conform to CSA C22.2 No. 24.

### Oil firing:

#### Operating controls: set-back thermostat, fan operating control switch with continuous operating switch, solenoid oil delay valve, burner, draft control.

#### Safety controls; flame safeguard-cadmium sulphide sensor, fan high limit control switch.

# Execution

## INSTALLATION

### Install in accordance with manufacturer's instructions, regulations of authorities having jurisdiction and to CAN/CSA-B139 and/or Canadian Electric Code.

### Co-ordinate with Section 03 30 00 – Cast-in-Place Concrete regarding concrete bases as indicated on drawings.

### Provide Owner written report of test results.

### Bacharach smoke density number not to exceed #1.

## Commissioning

### Manufacturer to:

#### Certify installation.

#### Start up and commission installation.

#### Carry out on-site performance verification tests.

#### Demonstrate operation and maintenance.

### Provide Owner at least 72 h notice prior to inspections, tests, and demonstrations. Submit written report of inspections and test results.

### Commission in accordance with Section 01 91 13.13 - Commissioning (Cx) Requirements.

### Final commissioning to occur between November and March when ambient temperature is -10oC or lower.

END OF SECTION